## Actual AC Split
PT. DAIKIN APPLIED SOLUTIONS INDONESIA
ACTUAL SERVICE HVAC AC SPLIT
PERIODE 01 - 31 MARET 2026
No | Date | Category | Floor | Area | Tenant | Merk | Capacity (PK) | Compressor Ampere | [9 empty] | Air Temperature (oC) | [5 empty] | Room Temperature |  |  | Air Flow (Ft/m) |  |  | Performa Unit (CFM) | Remarks
[8 empty] | Name Plate | Before |  |  | After |  |  | Margin |  |  | Supply |  | Margin | Return |  | Margin | (oC)
[9 empty] | R | S | T | R | S | T | R | S | T | Before | After |  | Before | After |  | Before | After | Margin | Before | After | Margin
1 | 2026-03-02 | F&B | LB | PISC | ACAII | LG | 2,5 PK / R32 | 11.5 | 10.4 |  |  | 10.5 |  |  | -0.1 | 0 | 0 | 13.4 | 12.8 | 0.6 | 24.1 | 23.6 | 0.5 | 22.9 | 22.3 | 0.6 | 932 | 982 | 50 | 2032.74 | NORMAL
2 | 2026-03-04 | F&B | LB | PISC | SALADSTOP! | DAIKIN | 2PK / R32 | 7.8 | 6.7 |  |  | 6.8 |  |  | -0.1 | 0 | 0 | 14.2 | 13.6 | 0.6 | 26 | 25.7 | 0.3 | 23.4 | 22.8 | 0.6 | 666 | 740 | 74 | 1531.8 | NORMAL
3 | 2026-03-03 | RETAIL | LB | PISC | GUDANG LOUIS VUITTON 001 | PANASONIC | 2,5 PK / R32 | 11.5 | 10.8 |  |  | 10.6 |  |  | 0.2 | 0 | 0 | 14.8 | 13.2 | 1.6 | 23.4 | 22.8 | 0.6 | 22.8 | 21.2 | 1.6 | 485 | 510 | 25 | 1055.7 | NORMAL
4 | 2026-03-03 | RETAIL | LB | PISC | GUDANG LOUIS VUITTON 002 | PANASONIC | 2,5 PK / R32 | 11.5 | 10.7 |  |  | 10 |  |  | 0.7 | 0 | 0 | 14.5 | 14 | 0.5 | 24 | 23.5 | 0.5 | 21.1 | 20.7 | 0.4 | 490 | 505 | 15 | 1045.35 | NORMAL
5 | 2026-03-03 | RETAIL | LB | PISC | GUDANG LOUIS VUITTON 003 | DAIKIN | 2,5 PK / R32 | 11.5 | 10.7 |  |  | 10.6 |  |  | 0.1 | 0 | 0 | 14.5 | 13.8 | 0.7 | 23 | 23 | 0 | 21.3 | 21.2 | 0.1 | 480 | 500 | 20 | 1035 | NORMAL
6 | 2026-03-07 | RETAIL | P2 | PISC | MEISO | DAIKIN | 1 PK / R22 | 4 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 15.1 | 14.5 | 0.6 | 23 | 22.3 | 0.7 | 21.7 | 21.6 | 0.1 | 366 | 394 | 28 | 815.58 | NORMAL
7 | 2026-03-06 | BOH | P2 | PISC | KLINIK PLAZA INDONESIA 001 | PANASONIC | 2PK / R32 | 7.8 | 5.6 |  |  | 5.4 |  |  | 0.2 | 0 | 0 | 15.1 | 14.4 | 0.7 | 24 | 23.1 | 0.9 | 22.9 | 22.6 | 0.3 | 607 | 638 | 31 | 1320.66 | NORMAL
8 | 2026-03-06 | BOH | P2 | PISC | KLINIK PLAZA INDONESIA 002 | PANASONIC | 1 PK / R22 | 4 | 3.7 |  |  | 3.6 |  |  | 0.1 | 0 | 0 | 12.7 | 12.5 | 0.2 | 23.8 | 23.9 | -0.1 | 22.6 | 22.1 | 0.5 | 346 | 385 | 39 | 796.95 | NORMAL
9 | 2026-03-08 | BOH | P2 | PISC | R. CALL CENTER | PANASONIC | 1 PK / R22 | 4 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 11.4 | 10.5 | 0.9 | 24 | 23.5 | 0.5 | 23 | 22.8 | 0.2 | 415 | 591 | 176 | 1223.37 | NORMAL
10 | 2026-03-07 | BOH | P2 | PISC | LOBBY LIFT 15-16 | DAIKIN | 2PK / R32 | 7.8 | 7.1 |  |  | 7 |  |  | 0.1 | 0 | 0 | 16.3 | 15 | 1.3 | 25.4 | 24.5 | 0.9 | 23 | 22.7 | 0.3 | 348 | 354 | 6 | 732.78 | NORMAL
11 | 2026-03-08 | BOH | P2 | PISC | OFFICE SECURE PARKING (R. ADMIN) | PANASONIC | ½ PK / R32 | 2 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 14.2 | 13.6 | 0.6 | 25.4 | 24.5 | 0.9 | 23 | 22.7 | 0.3 | 157 | 175 | 18 | 362.25 | NORMAL
12 | 2026-03-08 | BOH | P2 | PISC | OFFICE SECURE PARKING OPS 001 (R. CCTV) | DAIKIN | 1PK/R410 | 4 | 3.4 |  |  | 3.5 |  |  | -0.1 | 0 | 0 | 11.5 | 10.3 | 1.2 | 22.9 | 21.8 | 1.1 | 22.9 | 22 | 0.9 | 314 | 450 | 136 | 931.5 | NORMAL
13 | 2026-03-03 | BOH | P2 | PISC | OFFICE SECURE PARKING 001 (R. SERVER) | PANASONIC | 2PK / R32 | 7.8 | 6.7 |  |  | 6.8 |  |  | -0.1 | 0 | 0 | 14.2 | 13.6 | 0.6 | 24 | 23.7 | 0.3 | 23 | 22.7 | 0.3 | 666 | 740 | 74 | 1531.8 | NORMAL
14 | 2026-03-03 | BOH | P2 | PISC | OFFICE SECURE PARKING 002 (R. SERVER) | DAIKIN | 2PK / R32 | 7.8 | 7.2 |  |  | 7.1 |  |  | 0.1 | 0 | 0 | 14.3 | 13.5 | 0.8 | 24.2 | 23.8 | 0.4 | 23.1 | 22.8 | 0.3 | 711 | 790 | 79 | 1635.3 | NORMAL
15 | 2026-03-02 | BOH | P2 | PISC | POS SECURITY LOADING 001 | PANASONIC | ½ PK / R32 | 2 | 1.5 |  |  | 1.7 |  |  | -0.2 | 0 | 0 | 13.2 | 12.6 | 0.6 | 23.7 | 23.5 | 0.2 | 22.8 | 22.4 | 0.4 | 135 | 150 | 15 | 310.5 | NORMAL
16 | 2026-03-08 | BOH | P2 | PISC | R. PROVOST 001 | PANASONIC | 1 PK / R32 | 4 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 18.4 | 17.8 | 0.6 | 24.1 | 23.6 | 0.5 | 23 | 22.7 | 0.3 | 275 | 354 | 79 | 732.78 | NORMAL
17 | 2026-03-08 | BOH | P2 | PISC | R. PROVOST 002 | PANASONIC | ½ PK / R32 | 2 | 1.8 |  |  | 1.9 |  |  | -0.1 | 0 | 0 | 18 | 17 | 1 | 24 | 23.5 | 0.5 | 22 | 21 | 1 | 154 | 172 | 18 | 356.04 | NORMAL
18 | 2026-03-08 | BOH | P2 | PISC | R. PROVOST 004 (DEPAN) | PANASONIC | 1,5 PK/R22 | 5.5 | 2.8 |  |  | 3.1 |  |  | -0.3 | 0 | 0 | 18 | 17 | 1 | 23.8 | 23.7 | 0.1 | 23 | 22.6 | 0.4 | 513 | 570 | 57 | 1179.9 | NORMAL
19 | 2026-03-05 | BOH | P2 | PISC | R. PROVOST 005 (INTROGASI) | PANASONIC | 2PK / R32 | 7.8 | 7.3 |  |  | 7.3 |  |  | 0 | 0 | 0 | 12.7 | 12.5 | 0.2 | 21.8 | 21.5 | 0.3 | 21.8 | 21.5 | 0.3 | 666 | 740 | 74 | 1531.8 | NORMAL
20 | 2026-03-09 | BOH | P2 | PISC | R. MESIN LIFT 1-2 | PANASONIC | 1,5 PK/R22 | 5.5 | 4.2 |  |  | 4 |  |  | 0.2 | 0 | 0 | 12.1 | 10.8 | 1.3 | 24.2 | 23.6 | 0.6 | 23.5 | 22.1 | 1.4 | 432 | 563 | 131 | 1165.41 | NORMAL
21 | 2026-03-09 | BOH | P2 | PISC | R. MESIN LIFT 1-2 | PANASONIC | 1 PK/R32 | 4 | 3.2 |  |  | 3.3 |  |  | -0.1 | 0 | 0 | 22.5 | 11.8 | 10.7 | 23 | 22.9 | 0.1 | 23.8 | 22.7 | 1.1 | 654 | 833 | 179 | 1724.31 | NORMAL
22 | 2026-03-19 | BOH | P2 | PISC | R. BUILDING MAINTENANCE | PANASONIC | 2PK / R32 | 7.8 | 6.4 |  |  | 5.3 |  |  | 1.1 | 0 | 0 | 10.1 | 9.4 | 0.7 | 24 | 23.4 | 0.6 | 23.1 | 22.8 | 0.3 | 704 | 1008 | 304 | 2086.56 | NORMAL
23 | 2026-03-16 | BOH | P2 | PISC | TRASHROOM 001 | YORK | 5 PK / R410 | 12.5 | 7.1 |  |  | 7 |  |  | 0.1 | 0 | 0 | 17.4 | 16.1 | 1.3 | 23.9 | 23.8 | 0.1 | 22.7 | 22.3 | 0.4 | 1430 | 1587 | 157 | 3285.09 | NORMAL
24 | 2026-03-10 | BOH ENG | L48 | OFT | R. TRAFO LV-7 | YORK | 10 PK | 20.7 | 19.4 | 19.1 | 19.3 | 19.2 | 19 | 19.2 | 0.2 | 0.1 | 0.1 | 16.5 | 15 | 1.5 | 23.3 | 23 | 0.3 | 22.9 | 22.3 | 0.6 | 900 | 980 | 80 | 2028.6 | NORMAL
25 | 2026-03-19 | BOH | P2 | PISC | MASJID BAITURRAHMAN 010 | MC QUAY | 5 PK / R22 | 12.5 | 10.5 | 10.3 | 10.6 | 10.6 | 10.3 | 10.5 | -0.1 | 0 | 0.1 | 19.3 | 18 | 1.3 | 24 | 23.6 | 0.4 | 23.5 | 22.6 | 0.9 | 702 | 781 | 79 | 1616.67 | NORMAL
26 | 2026-03-09 | BOH | P2 | PISC | CORRIDOR LIFT 7-8 | DAIKIN | ½ PK / R32 | 2 | 1.5 |  |  | 1.6 |  |  | -0.1 | 0 | 0 | 13.8 | 11.6 | 2.2 | 24.7 | 24.6 | 0.1 | 23.4 | 22.9 | 0.5 | 508 | 577 | 69 | 1194.39 | NORMAL
27 | 2026-03-07 | BOH | P2 | PISC | R. CSO PRIA | DAIKIN | 1PK/R32 | 4 | 6.8 |  |  | 7.2 |  |  | -0.4 | 0 | 0 | 17 | 16.7 | 0.3 | 23.3 | 22.8 | 0.5 | 22.8 | 22.2 | 0.6 | 600 | 705 | 105 | 1459.35 | NORMAL
28 | 2026-03-07 | BOH | P2 | PISC | R. CSO WANITA | PANASONIC | 2PK / R32 | 7.8 | 6.8 |  |  | 7.1 |  |  | -0.3 | 0 | 0 | 17.5 | 17 | 0.5 | 23.3 | 22.6 | 0.7 | 23 | 22.8 | 0.2 | 711 | 790 | 79 | 1635.3 | NORMAL
29 | 2026-03-12 | BOH | P2 | PISC | LOCKER MINIAPOLIS PRIA | DAIKIN | 2PK / R32 | 7.8 | 6.71 |  |  | 6.46 |  |  | 0.3 | 0 | 0 | 18.3 | 18.1 | 0.2 | 26 | 25.7 | 0.3 | 23 | 22.3 | 0.7 | 666 | 740 | 74 | 1531.8 | NORMAL
30 | 2026-03-12 | BOH | P2 | PIE | LOCKER MINIAPOLIS WANITA | DAIKIN | 2PK / R32 | 7.8 | 6.72 |  |  | 6.48 |  |  | 0.2 | 0 | 0 | 18.4 | 17.2 | 1.2 | 26.2 | 25.6 | 0.6 | 22.8 | 22.4 | 0.4 | 711 | 790 | 79 | 1635.3 | NORMAL
31 | 2026-03-11 | BOH | P2 | PIE | TOILET CSO WANITA | DAIKIN | 2PK / R32 | 7.8 | 3.6 |  |  | 3.4 |  |  | 0.2 | 0 | 0 | 17 | 15 | 2 | 24 | 23.4 | 0.6 | 23.1 | 22.6 | 0.5 | 550 | 617 | 67 | 1277.19 | NORMAL
32 | 2026-03-30 | BOH | P2 | PIE | OFFICE SECURITY PT. AMAN | YORK YSB 54 | 10PK/R407 | 20.7 | 19.5 | 19.5 | 19.3 | 19.6 | 19.2 | 19.3 | -0.1 | 0.3 | 0 | 14 | 13.5 | 0.5 | 26.3 | 25.7 | 0.6 | 23.1 | 22.8 | 0.3 | 504 | 560 | 56 | 1159.2 | NORMAL
33 | 2026-03-10 | BOH | P2 | PIE | OFFICE GHP | YORK YSB 54 | 5PK/R407 | 12.5 | 10.5 | 10.3 | 10.6 | 10.6 | 10.3 | 10.5 | -0.1 | 0 | 0.1 | 19 | 14 | 5 | 23.9 | 23.5 | 0.4 | 22.8 | 21.2 | 1.6 | 464 | 988 | 524 | 2045.16 | NORMAL
34 | 2026-03-31 | BOH | P2 | PIE | R. BKO | YORK YSB 54 | 5PK/R407 | 12.5 | 10.6 | 10.4 | 10.5 | 10.4 | 10.3 | 10.7 | 0.2 | 0.1 | -0.2 | 9.2 | 8.7 | 0.5 | 25.3 | 24.5 | 0.8 | 22.9 | 21.8 | 1.1 | 398 | 476 | 78 | 985.32 | NORMAL
35 | 2026-03-07 | BOH | P2 | PIE | LOCKER SECURITY NIGHT GUARD 001 | DAIKIN | 2PK / R32 | 7.8 | 6.1 |  |  | 6.3 |  |  | -0.2 | 0 | 0 | 21.3 | 19.1 | 2.2 | 24.3 | 23.1 | 1.2 | 21.4 | 21.3 | 0.1 | 341 | 376 | 35 | 778.32 | NORMAL
36 | 2026-03-07 | BOH | P2 | PIE | LOCKER SECURITY NIGHT GUARD 002 | PANASONIC | 2PK / R32 | 7.8 | 6.4 |  |  | 6.5 |  |  | -0.1 | 0 | 0 | 21.4 | 18.3 | 3.1 | 23.5 | 22.5 | 1 | 21.8 | 21.3 | 0.5 | 367 | 376 | 9 | 778.32 | NORMAL
37 | 2026-03-14 | BOH | P2 | PIE | KANTINA 001 | DAIKIN | 1PK/R32 | 4 | 3.3 |  |  | 3.2 |  |  | 0.1 | 0 | 0 | 12.2 | 8.8 | 3.4 | 23.2 | 22.8 | 0.4 | 23 | 22.5 | 0.5 | 459 | 510 | 51 | 1055.7 | NORMAL
38 | 2026-03-13 | SALON | P2 | PIE | PAXI PLUS | PANASONIC | 2PK / R32 | 7.8 | 6.58 |  |  | 6.2 |  |  | 0.4 | 0 | 0 | 6.8 | 6.7 | 0.1 | 14.2 | 13.7 | 0.5 | 24.1 | 23.6 | 0.5 | 303 | 449 | 146 | 929.43 | NORMAL
39 | 2026-03-14 | BOH | P2 | PIE | R. MITSUBISHI | PANASONIC | 2PK / R32 | 7.8 | 3.35 | [5 empty] | 3.4 | 0 | 0 | 18 | 15 | 3 | 24.5 | 24 | 0.5 | 23.2 | 22.5 | 0.7 | 297 | 425 | 128 | 879.75 | NORMAL
40 | 2026-03-13 | BOH | P3 | PIE | LOCKER GHP PRIA | PANASONIC | 1,5 PK R22 | 5.5 | 3.27 |  |  | 3.32 |  |  | 0 | 0 | 0 | 13.2 | 8 | 5.2 | 23.8 | 23.7 | 0.1 | 23.7 | 21.9 | 1.8 | 216 | 250 | 34 | 517.5 | NORMAL
41 | 2026-03-13 | BOH | P3 | PIE | LOCKER GHP WANITA | PANASONIC | 1 PK / R32 | 4 | 3.69 |  |  | 4.02 |  |  | -0.3 | 0 | 0 | 10.5 | 8.5 | 2 | 26 | 25.7 | 0.3 | 22.9 | 21.6 | 1.3 | 320 | 370 | 50 | 765.9 | NORMAL
42 | 2026-03-17 | RETAIL | P3 | PISC | COLOR WASH | DAIKIN | 1 PK / R32 | 4 | 7.6 |  |  | 6.3 |  |  | 1.3 | 0 | 0 | 16.3 | 16 | 0.3 | 23.8 | 23.2 | 0.6 | 19.1 | 18.7 | 0.4 | 551 | 686 | 135 | 1418.985 | NORMAL
43 | 2026-03-15 | BOH | P3 | PISC | R. DRIVER TENGAH | DAIKIN | 1 PK / R32 | 4 | 6.4 |  |  | 7 |  |  | -0.6 | 0 | 0 | 10.1 | 8.4 | 1.7 | 26 | 25.7 | 0.3 | 20.1 | 19.5 | 0.6 | 671 | 1012 | 341 | 2094.84 | NORMAL
44 | 2026-03-06 | BOH | P3 | PISC | GUDANG LOGISTIK 001 | PANASONIC | 1 PK / R22 | 4 | 4.5 |  |  | 6.2 |  |  | -1.7 | 0 | 0 | 12.8 | 12.5 | 0.3 | 25 | 24.7 | 0.3 | 22.8 | 21.7 | 1.1 | 435 | 457 | 22 | 945.99 | NORMAL
45 | 2026-03-31 | BOH | P3 | PISC | JNE | DAIKIN | 1 PK / R32 | 4 | 3.3 |  |  | 3.5 |  |  | -0.2 | 0 | 0 | 14.3 | 13.4 | 0.9 | 24.2 | 23.5 | 0.7 | 23 | 22.6 | 0.4 | 342 | 381 | 39 | 788.67 | NORMAL
46 | 2026-03-10 | BOH | P3 | PISC | LOCKER KORLAP SECURE PARKING | PANASONIC | 1 PK / R22 | 4 | 3.4 |  |  | 2.44 |  |  | 1 | 0 | 0 | 18 | 15 | 3 | 24 | 23.6 | 0.4 | 22.9 | 21.6 | 1.3 | 333 | 370 | 37 | 765.9 | NORMAL
47 | 2026-03-13 | BOH | P3 | PISC | OFFICE SECURE PARKING (R. OPERATION) | PANASONIC | 2,5 PK / R32 | 11.5 | 8 |  |  | 7.8 |  |  | 0.2 | 0 | 0 | 14.2 | 13.6 | 0.6 | 24.1 | 23.5 | 0.6 | 23 | 22.7 | 0.3 | 855 | 950 | 95 | 1966.5 | NORMAL
48 | 2026-03-31 | BOH | P3 | PISC | OFFICE SECURE PARKING (R. PENGAWAS) | PANASONIC | 2PK / R32 | 7.8 | 3.1 |  |  | 3.05 |  |  | 0.1 | 0 | 0 | 12.8 | 11.2 | 1.6 | 25 | 24.3 | 0.7 | 23.4 | 22.7 | 0.7 | 472 | 510 | 38 | 1055.7 | NORMAL
49 | 2026-03-11 | BOH | P3 | PISC | OFFICE SECURE PARKING (LOCKER WANITA) | PANASONIC | 1 PK / R32 | 4 | 3.29 |  |  | 3.52 |  |  | -0.2 | 0 | 0 | 17 | 15 | 2 | 24.2 | 23.8 | 0.4 | 23.5 | 22.8 | 0.7 | 529 | 786 | 257 | 1627.02 | NORMAL
50 | 2026-03-15 | BOH | P3 | PISC | OFFICE KING VALET | PANASONIC | 2,5 PK / R32 | 11.5 | 2.8 |  |  | 2.5 |  |  | 0.3 | 0 | 0 | 14.1 | 13.6 | 0.5 | 25.5 | 24.5 | 1 | 21.4 | 20.5 | 0.9 | 488 | 529 | 41 | 1095.03 | NORMAL
51 | 2026-03-13 | BOH | P3 | PISC | R. DRIVER K05 N | DAIKIN | 2,5 PK / R32 | 11.5 | 6.2 |  |  | 6.4 |  |  | -0.2 | 0 | 0 | 18.4 | 17.3 | 1.1 | 25 | 24.7 | 0.3 | 23.1 | 21.5 | 1.6 | 844 | 889 | 45 | 1840.23 | NORMAL
52 | 2026-03-16 | BOH ENG | P3 | PISC | R. PANEL STP | DAIKIN | 2PK / R32 | 7.8 | 3.8 |  |  | 3.5 |  |  | 0.3 | 0 | 0 | 16.2 | 15.6 | 0.6 | 26 | 25.7 | 0.3 | 23.1 | 22.8 | 0.3 | 761 | 779 | 18 | 1612.53 | NORMAL
53 | 2026-03-17 | BOH ENG | P3 | PISC | R. LAB BIOSANT | PANASONIC | 1,5 PK/R22 | 5.5 | 3.9 |  |  | 4 |  |  | -0.1 | 0 | 0 | 13.2 | 12.6 | 0.6 | 23.8 | 23.7 | 0.1 | 22.9 | 22.5 | 0.4 | 513 | 570 | 57 | 1179.9 | NORMAL
54 | 2026-03-17 | BOH ENG | P3 | PISC | R. PANEL POMPA SW | PANASONIC | 2PK / R32 | 7.8 | 5.2 |  |  | 5.3 |  |  | -0.1 | 0 | 0 | 15.1 | 14.4 | 0.7 | 24 | 23.1 | 0.9 | 22.9 | 22.6 | 0.3 | 607 | 638 | 31 | 1320.66 | NORMAL
55 | 2026-03-16 | BOH | P3 | PISC | R. MESIN LIFT 7 - 8 | PANASONIC | 1 PK / R32 | 4 | 3.3 |  |  | 3.2 |  |  | 0.1 | 0 | 0 | 14.1 | 13.4 | 0.7 | 24 | 23.6 | 0.4 | 23.2 | 22.1 | 1.1 | 333 | 370 | 37 | 765.9 | NORMAL
56 | 2026-03-29 | BOH | P4 | PIE | KOPERASI PATEN | PANASONIC | 2PK / R32 | 7.8 | 5.7 |  |  | 5.6 |  |  | 0.1 | 0 | 0 | 15.7 | 14.2 | 1.5 | 24 | 23.4 | 0.6 | 22.8 | 22.6 | 0.2 | 750 | 617 | -133 | 1277.19 | NORMAL
57 | 2026-03-29 | BOH | P4 | PIE | KOPERASI PATEN | PANASONIC | 2PK / R32 | 7.8 | 6.2 |  |  | 6.1 |  |  | 0.1 | 0 | 0 | 16.3 | 15 | 1.3 | 24 | 23.5 | 0.5 | 23 | 22.8 | 0.2 | 574 | 613 | 39 | 1268.91 | NORMAL
58 | 2026-03-29 | BOH | P4 | PIE | R. KETUA KOPERASI PATEN | PANASONIC | 1 PK/R22 | 4 | 3.8 |  |  | 3.5 |  |  | 0.3 | 0 | 0 | 16.2 | 14.3 | 1.9 | 24.1 | 23 | 1.1 | 22.6 | 22.1 | 0.5 | 704 | 791 | 87 | 1637.37 | NORMAL
59 | 2026-03-07 | BOH | L2 | PISC | MULTI FUNTION HALL 001 A | YORK | R22/10PK | 20.7 | 19.4 | 19.1 | 19.3 | 19.2 | 19 | 19.2 | -0.2 | -0.1 | -0.1 | 16.5 | 15 | 1.5 | 24.3 | 23.6 | 0.7 | 23.9 | 23.4 | 0.5 | 900 | 980 | 80 | 2028.6 | NORMAL
60 | 2026-03-07 | BOH | L2 | PISC | MULTI FUNTION HALL 002 B 1 | ACOOL | R22/10PK | 20.7 | 19.3 | 19 | 19.1 | 19.2 | 19 | 19.2 | -0.1 | 0 | 0.1 | 14.3 | 13.5 | 0.8 | 25.6 | 24.8 | 0.8 | 23.1 | 22.7 | 0.4 | 866 | 963 | 97 | 1993.41 | NORMAL
61 | 2026-03-07 | BOH | L2 | PISC | MULTI FUNTION HALL 003 B 2 | YORK | R22/10PK | 20.7 | 19.5 | 19.3 | 19.4 | 19.5 | 19.3 | 19.5 | 0 | 0 | 0.1 | 17.3 | 16.7 | 0.6 | 24 | 23.5 | 0.5 | 23.5 | 22.6 | 0.9 | 684 | 760 | 76 | 1573.2 | NORMAL
62 | 2026-03-07 | BOH | L2 | PISC | MULTI FUNTION HALL 004 C 1 | YORK | R22/10PK | 20.7 | 19.5 | 19.5 | 19.3 | 19.6 | 19.2 | 19.3 | 0.1 | -0.3 | 0 | 15 | 14.5 | 0.5 | 25.3 | 24.7 | 0.6 | 23.1 | 22.8 | 0.3 | 504 | 560 | 56 | 1159.2 | NORMAL
63 | 2026-03-07 | BOH | L2 | PISC | MULTI FUNTION HALL 006 D | YORK | R22/10PK | 20.7 | 19.3 | 19 | 19.1 | 19.2 | 19 | 19.2 | -0.1 | 0 | 0.1 | 16.4 | 15.3 | 1.1 | 25.9 | 25.1 | 0.8 | 23.5 | 22.9 | 0.6 | 788 | 793 | 5 | 1641.51 | NORMAL
|  |  |  | PT Daikin Applied Solutions Indonesia, |  |  | Diperiksa oleh, | [10 empty] | Diketahui oleh, | [8 empty] | Disetujui oleh,
|  |  |  | ( Raditya Yogaswara ) |  |  | ( Ahmad Zani ) | [10 empty] | (Agus Bintoro) | [8 empty] | (Mohammad Riva Noor H)
|  |  |  | Field & Application Engineer |  |  | Spv. BM Operasional & Maintenance | [10 empty] | Operational Retail & Office Section Head | [8 empty] | Operational Facility Manager Retail
PERIODE 1 - 30 APRIL 2026
No |  | Category | Floor | Area | Tenant | Merk | Capacity (PK) | Compressor Ampere | [9 empty] | Air Temperature (oC) | [5 empty] | Room Temperature |  |  | Air Flow (Ft/m) |  |  | Performa Unit (CFM) | Remarks
[8 empty] | Name Plate | Before |  |  | After |  |  | Margin |  |  | Return |  | Margin | Supply |  | Margin | (oC)
[9 empty] | R | S | T | R | S | T | R | S | T | Before | After |  | Before | After |  | Before | After | Margin | Before | After | Margin
1 |  | BOH | P1 | PISC | POS J (POS KELUAR GHJ) | PANASONIC | 0,5 PK/R32 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
2 | 2026-04-03 | BOH | P1 | PISC | R. SECURITY OT 1 | DAIKIN | 1 PK/R32 |  | 3.6 |  |  | 3.3 |  |  | -0.3 |  |  | 16.2 | 15.4 | -0.8 | 22.5 | 21.9 | -0.6 | 21.2 | 20.4 | -0.8 | 493 | 581 | 88 |  | NORMAL
3 | 2026-04-03 | BOH | P1 | PISC | R. SECURITY OT 2 | DAIKIN | 1 PK/R32 |  | 3.8 |  |  | 3.3 |  |  | -0.5 |  |  | 16.2 | 15.4 | -0.8 | 21.9 | 21.6 | -0.3 | 21.2 | 20.4 | -0.8 | 462 | 571 | 109 |  | NORMAL
4 | 2026-04-01 | BOH | P1 | PISC | R. OFFICE GHP | DAIKIN | 1 PK/R32 |  | 3.5 |  |  | 3.2 |  |  | -0.3 |  |  | 17.4 | 16.3 | -1.1 | 22.1 | 21.5 | -0.6 | 21.9 | 21.2 | -0.7 | 338 | 547 | 209 |  | NORMAL
5 | 2026-04-01 | BOH ENG | P1 | PISC | R. GENSET DIESEL HYATT | PANASONIC | 2 PK/R32 |  | 8.9 |  |  | 7.8 |  |  | -1.1 |  |  | 28.8 | 28 | -0.8 | 30.2 | 29.8 | -0.4 | 23.9 | 23.5 | -0.4 | 472 | 520 | 48 |  | NORMAL
6 |  | BOH ENG | P1 | PISC | R. GENSET DIESEL HYATT | PANASONIC | 2 PK/R32 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit rusak
7 |  | BOH ENG | P1 | PISC | R. GENSET DIESEL HYATT | PANASONIC | 2 PK/R32 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit rusak
8 | 2026-04-05 | BOH | P1 | PIE | POS SECURITY THAMRIN | PANASONIC | 0.5 PK/R32 |  | 2.3 |  |  | 2.1 |  |  | -0.2 |  |  | 20.5 | 19.1 | -1.4 | 22.4 | 21.9 | -0.5 | 23.5 | 23.1 | -0.4 | 214 | 254 | 40 |  | NORMAL
9 | 2026-04-04 | BOH | P1 | PIE | R. SECURITY PIR 001 | DAIKIN | 2 PK/R32 |  | 7.2 |  |  | 6.9 |  |  | -0.3 |  |  | 15.2 | 14.7 | -0.5 | 20.3 | 19.8 | -0.5 | 20.5 | 19.6 | -0.9 | 572 | 598 | 26 |  | NORMAL
10 | 2026-04-04 | BOH | P1 | PIE | R. SECURITY PIR 002 | DAIKIN | 2 PK/R32 |  | 6.9 |  |  | 6.8 |  |  | -0.1 |  |  | 15.9 | 15.2 | -0.7 | 20.8 | 20.3 | -0.5 | 20.8 | 20.1 | -0.7 | 498 | 520 | 22 |  | NORMAL
11 | 2026-04-06 | BOH | P1 | PIE | R. SECURITY PIR 003 | DAIKIN | 2 PK/R32 |  | 7.4 |  |  | 7.3 |  |  | -0.1 |  |  | 17 | 16.1 | -0.9 | 21.6 | 20.8 | -0.8 | 19.9 | 19.3 | -0.6 | 472 | 521 | 49 |  | NORMAL
12 | 2026-04-06 | BOH | P1 | PIE | R. SECURITY PIR 004 | DAIKIN | 1 PK/R32 |  | 3.9 |  |  | 3.7 |  |  | -0.2 |  |  | 18.5 | 17.2 | -1.3 | 20.1 | 19.7 | -0.4 | 22.7 | 21.1 | -1.6 | 475 | 519 | 44 |  | NORMAL
13 | 2026-04-06 | BOH | P1 | PIE | R. SECURITY PIR 005 | DAIKIN | 1 PK/R32 |  | 3.7 |  |  | 3.6 |  |  | -0.1 |  |  | 17.6 | 16.2 | -1.4 | 19.9 | 19.3 | -0.6 | 22.7 | 21.1 | -1.6 | 450 | 576 | 126 |  | NORMAL
14 | 2026-04-07 | BOH | P1 | PIE | R. LOGISTIC SECURITY | DAIKIN | 1 PK/R32 |  | 3.9 |  |  | 3.5 |  |  | -0.4 |  |  | 19.2 | 18.1 | -1.1 | 22.5 | 21.9 | -0.6 | 24.2 | 23.3 | -0.9 | 482 | 515 | 33 |  | NORMAL
15 |  | BOH | P1 | PIE | LOBBY LIFT CP | DAIKIN | 2 PK/R2 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit rusak
16 | 2026-04-02 | BOH | P1 | PIE | R. TUNGGU DRIVER | DAIKIN | 1 PK/R32 |  | 3.6 |  |  | 3.4 |  |  | -0.2 |  |  | 16.1 | 15.7 | -0.4 | 21.4 | 21.1 | -0.3 | 21.9 | 21.1 | -0.8 | 452 | 561 | 109 |  | NORMAL
17 |  | BOH | P1 | PIE | LOBBY LIFT CP 001 | UCHIDA | 0,75 PK | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | RESCHEDULE
18 |  | BOH | P1 | PIE | LOBBY LIFT CP 002 | UCHIDA | 0,75 PK | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | RESCHEDULE
19 |  | BOH | P1 | PIE | LOBBY LIFT CP 003 | UCHIDA | 0,75 PK | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | RESCHEDULE
20 | 2026-04-07 | BOH | P1 | PIE | R. MITSUBISHI | PANASONIC | 1 PK/R32 |  | 3.4 |  |  | 3.4 |  |  | 0 |  |  | 22.6 | 21.4 | -1.2 | 25.3 | 24.8 | -0.5 | 26.5 | 25.9 | -0.6 | 485 | 530 | 45 |  | NORMAL
21 | 2026-04-26 | RETAIL | P1 | PIE | MEISO | PANASONIC | 2 PK / R32 |  | 6.48 |  |  | 6.34 |  |  | -0.14 |  |  | 18.4 | 17.7 | -0.7 | 22.5 | 21.3 | -1.2 | 22.8 | 21.5 | -1.3 | 347.8 | 539.4 | 191.6 |  | NORMAL
22 | 2026-04-26 | BOH ENG | P1 | OFT | R. MSB | MIDEA | 6 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit rusak
23 | 2026-04-26 | BOH ENG | P1 | OFT | R. MSB | LG | 5 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit rusak
24 | 2026-04-26 | BOH ENG | P1 | OFT | R. MSB | LG | 5 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
25 | 2026-04-08 | BOH ENG | P1 | OFT | R. TX-29-30 | LG | 5 PK/R22 |  | 11.9 | 11.8 | 8.6 | 9.1 | 10 | 8.8 | -2.8 | -1.8 | 0.2 | 20.1 | 18.9 | -1.2 | 23.8 | 23.3 | -0.5 | 23.4 | 22.6 | -0.8 | 475 | 596 | 121 |  | NORMAL
26 |  | BOH ENG | P1 | OFT | R. TX-29-30 | LG | 6 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
27 |  | BOH ENG | P1 | OFT | R. TX-29-30 | LG | 6 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
28 |  | BOH ENG | P1 | OFT | R. TX-29-30 | LG | 6 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
29 |  | BOH ENG | P1 | OFT | R. TX-29-30 | LG | 6 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
30 |  | BOH ENG | P1 | OFT | R. TX-29-30 | LG | 6 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
31 | 2026-04-28 | BOH ENG | P1 | OFT | R. MCC 3 | LG | 6 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
32 | 2026-04-08 | BOH ENG | P1 | OFT | R. UPS | PANASONIC | 2 PK/R32 |  | 8.9 |  |  | 8.7 |  |  | -0.2 |  |  | 30.5 | 28.1 | -2.4 | 33.1 | 32.3 | -0.8 | 31.6 | 30.5 | -1.1 | 472 | 560 | 88 |  | NORMAL
33 | 2026-04-28 | BOH ENG | P1 | OFT | R. LV-11 | PANASONIC | 2 PK/R32 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
34 | 2026-04-28 | BOH ENG | P1 | OFT | R. TX-27 | MIDEA | 6 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
35 | 2026-04-28 | BOH ENG | P1 | OFT | R. TX-27 | LG | 6 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
36 | 2026-04-25 | BOH ENG | P1 | OFT | R. LV-8 | LG | 3 PK | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
37 | 2026-04-25 | BOH ENG | P1 | OFT | R. LV-8 | PANASONIC | 2 PK | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
38 | 2026-04-25 | BOH ENG | P1 | OFT | R. LV-8 | PANASONIC | 2 PK | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
39 | 2026-04-20 | F&B | L1 | PISC | OSTERIA GIA 001 | SAMSUNG | 2,5 PK?R22 |  | 17.38 | 18.17 | 16.14 | 13.3 | 10.22 | 8.49 | -4.08 |  |  | 18.4 | 16.8 | -1.6 | 22.6 | 21.8 | -0.8 | 22.5 | 21 | -1.5 | 129.8 | 328.9 | 199.1 |  | NORMAL
40 | 2026-04-20 | F&B | L1 | PISC | OSTERIA GIA 002 | SAMSUNG | 2,5 PK?R23 |  | 17.38 | 18.17 | 16.14 | 13.3 | 10.22 | 8.49 | -4.08 |  |  | 18.2 | 17.1 | -1.1 | 22.4 | 21.5 | -0.9 | 22.3 | 20.9 | -1.4 | 573.2 | 701.3 | 128.1 |  | NORMAL
41 | 2026-04-23 | F&B | L1 | PISC | SHABU-SHABU HOUSE 001 | YORK | 6 PK/R410A |  | 11.57 | 11.45 | 11.27 | 11.06 | 10.61 | 10.55 | -0.51 |  |  | 17.7 | 16.8 | -0.9 | 21.8 | 21.1 | -0.7 | 21.9 | 21.3 | -0.6 | 667.2 | 719.8 | 52.6 |  | NORMAL
42 | 2026-04-23 | F&B | L1 | PISC | SHABU-SHABU HOUSE 002 | YORK | 6 PK/R410A |  | 12.48 | 11.73 | 11.94 | 11.96 | 11.53 | 12.38 | -0.52 |  |  | 17.9 | 16.9 | -1 | 22 | 21.2 | -0.8 | 21.9 | 21.3 | -0.6 | 659.1 | 744.6 | 85.5 |  | NORMAL
43 |  | RETAIL | L1 | PISC | TIFFANY & CO | DAIKIN | 8 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Partisi
44 | 2026-04-21 | F&B | L1 | PISC | CHANEL TEMPORARY | YORK | 5 PK/R410A |  | 8.9 | 8.8 | 8.9 | 8.6 | 8.4 | 8.5 | -0.3 | -0.4 | -0.4 | 18.1 | 17.5 | -0.6 | 23.1 | 21.9 | -1.2 | 23.4 | 21.5 | -1.9 | 402.4 | 559.8 | 157.4 |  | NORMAL
45 | 2026-04-30 | F&B | L1 | PISC | VENCHY | YORK | SBH 50 DW |  | 4.1 | 3.9 | 3.84 | 4 | 3.86 | 3.79 | -0.1 | -0.04 | -0.05 | 17.8 | 17.2 | -0.6 | 21.4 | 20.9 | -0.5 | 21.9 | 21.2 | -0.7 | 674 | 723.5 | 49.5 |  | NORMAL
46 |  | BOH | L1 | PISC | CORRIDOR LOBBY TIMUR 001 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | UNIT TIDAK ADA
47 |  | BOH | L1 | PISC | CORRIDOR LOBBY TIMUR 002 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | UNIT TIDAK ADA
48 | 2026-04-10 | BOH ENG | L1 | PISC | R. MSA | DAIKIN | 2 PK/R22 |  | 3.6 |  |  | 3.4 |  |  | -0.2 |  |  | 22.5 | 21.4 | -1.1 | 26.3 | 25.9 | -0.4 | 24.6 | 23.5 | -1.1 | 472.7 | 560.1 | 87.4 |  | NORMAL
49 | 2026-04-10 | BOH ENG | L1 | PISC | R. MSA | DAIKIN | 2 PK/R32 |  | - |  |  | - |  |  | - |  |  | - | - | - | - | - | - | - | - | - |  |  | 0 |  | Unit Rusak
50 | 2026-04-10 | BOH ENG | L1 | PISC | R. MSA | DAIKIN | 8 PK/R22 |  | - |  |  | - |  |  | - |  |  | - | - | - | - | - | - | - | - | - |  |  | 0 |  | Unit Rusak
51 |  | BOH | L2 | PISC | MULTI FUNTION HALL 005 C 2 | CARRIER | 10 PK/R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
52 |  | RETAIL | LB | PISC | SALAD STOP | DAIKIN | [8 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | -
53 | 2026-04-12 | BOH ENG | L3 | PISC | R. KONTROL GAS ENGINEERING | DAIKIN | 2 PK/R32 |  | 6.92 |  |  | 6.81 |  |  | -0.11 |  |  | 30.1 | 26.2 | -3.9 | 33.4 | 32.9 | -0.5 | 30.3 | 28.3 | -2 | 316 | 510 | 194 |  | NORMAL
54 | 2026-04-12 | BOH ENG | L3 | PISC | R. KONTROL GAS ENGINEERING | DAIKIN | 2 PK/R32 |  | 7.05 |  |  | 6.65 |  |  | -0.4 |  |  | 21.9 | 21.4 | -0.5 | 24.7 | 23.3 | -1.4 | 28.1 | 27.1 | -1 | 347 | 511 | 164 |  | NORMAL
55 | 2026-04-12 | BOH ENG | L3 | PISC | R. KONTROL GAS ENGINEERING | PANASONIC | 2 PK/R32 |  | 7.12 |  |  | 6.98 |  |  | -0.14 |  |  | 22 | 20.1 | -1.9 | 24.8 | 23.9 | -0.9 | 26.8 | 25.3 | -1.5 | 382 | 534 | 152 |  | NORMAL
56 | 2026-04-12 | BOH ENG | L3 | PISC | R. KONTROL GAS ENGINEERING | PANASONIC | 2 PK/R22 |  | 6.91 |  |  | 7.19 |  |  | 0.28 |  |  | 22.5 | 21 | -1.5 | 25 | 24.4 | -0.6 | 26.1 | 25 | -1.1 | 331 | 502 | 171 |  | NORMAL
57 |  | BOH ENG | L3 | PISC | R. PANEL GAS ENGINEERING | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | -
58 |  | BOH ENG | L3 | PISC | R. PANEL GAS ENGINEERING | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | -
59 | 2026-04-19 | BOH ENG | L3 | PISC | R. PANEL GAS ENGINEERING | PANASONIC | 2 PK/R32 |  | 7.11 |  |  | 7.02 |  |  | -0.09 |  |  | 20.1 | 18.6 | -1.5 | 23.2 | 22.1 | -1.1 | 23.2 | 22.1 | -1.1 | 476 | 502 | 26 |  | NORMAL
60 | 2026-04-21 | BOH | L4 | PISC | R. SOUND SYSTEM ENGINEERING | DAIKIN | 2 PK/R32 |  | 6.04 |  |  | 5.96 |  |  | -0.08 |  |  | 23.2 | 22.1 | -1.1 | 25.3 | 24.6 | -0.7 | 26.1 | 25.6 | -0.5 | 407.5 | 621.8 | 214.3 |  | NORMAL
61 | 2026-04-14 | BOH ENG | L4 | PISC | R. VSD ENGINEERING | DAIKIN | 2 PK/R32 |  | 7.4 |  |  | 7.5 |  |  | 0.1 |  |  | 18.1 | 17.2 | -0.9 | 21.7 | 21.3 | -0.4 | 30 | 29.7 | -0.3 | 448 | 532 | 84 |  | NORMAL
62 | 2026-04-14 | BOH ENG | L4 | PISC | MUSHOLLA ENGINEERING | PANASONIC | 0,5 PK/R32 |  | 1.6 |  |  | 1.5 |  |  | -0.1 |  |  | 19 | 18.7 | -0.3 | 22 | 21.5 | -0.5 | 22.5 | 21.3 | -1.2 | 331.5 | 469.1 | 137.6 |  | NORMAL
63 | 2026-04-21 | BOH ENG | L4 | PISC | R. UPS ENGINEERING | DAIKIN | 1,5 PK/R32 |  | 1.55 |  |  | 1.55 |  |  | 0 |  |  | 14.2 | 12.8 | -1.4 | 19 | 18.4 | -0.6 | 16.4 | 14.9 | -1.5 | 348.2 | 481.2 | 133 |  | NORMAL
64 | 2026-04-19 | BOH ENG | L4 | PISC | R. MEETING ENGINEERING | PANASONIC | 2 PK/R32 |  | 6.8 |  |  | 6.6 |  |  | -0.2 |  |  | 18.3 | 17.6 | -0.7 | 20.3 | 19 | -1.3 | 20.5 | 19.8 | -0.7 | 450.6 | 559.1 | 108.5 |  | NORMAL
65 |  | BOH ENG | L4 | PISC | R. MB ENGINEERING | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | -
66 | 2026-04-18 | BOH ENG | L4 | PISC | R. MB ENGINEERING | PANASONIC | 2 PK / R22 |  | 6.4 |  |  | 5.9 |  |  | -0.5 |  |  | 15.6 | 14.8 | -0.8 | 23.5 | 22.7 | -0.8 | 23.4 | 22.6 | -0.8 | 376 | 521 | 145 |  | NORMAL
67 | 2026-04-18 | BOH ENG | L4 | PISC | R. KONTROL CHIILER ENGINEERING | PANASONIC | 2 PK / R32 |  | 6.4 |  |  | 5.9 |  |  | -0.5 |  |  | 19.2 | 18.7 | -0.5 | 23.5 | 22.6 | -0.9 | 23.1 | 22.3 | -0.8 | 406 | 493 | 87 |  | NORMAL
68 | 2026-04-18 | BOH ENG | L4 | PISC | R. KONTROL CHIILER ENGINEERING | PANASONIC | 2,5 PK / R22 |  | 15.1 |  |  | 13.7 |  |  | -1.4 |  |  | 16.5 | 15.3 | -1.2 | 24.6 | 24 | -0.6 | 24.3 | 23.9 | -0.4 | 411 | 534 | 123 |  | NORMAL
69 |  | BOH ENG | L4 | PISC | R. DIESEL GENSET HYATT | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | -
70 | 2026-04-23 | BOH ENG | L5 | PIE | R. TRAVO CHILLER | LG | 9 PK / R22 |  | 16.8 | 14 | 13.5 | 17 | 13.3 | 12.2 | 0.2 |  |  | 17.3 | 16.8 | -0.5 | 24.1 | 23.5 | -0.6 | 23.6 | 22.9 | -0.7 | 709.2 | 867.4 | 158.2 |  | NORMAL
71 | 2026-04-23 | BOH ENG | L5 | PIE | R. TRAVO CHILLER | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
72 | 2026-04-23 | BOH ENG | L5 | PIE | R. PANEL CHILLER | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
73 | 2026-04-23 | BOH ENG | L5 | PIE | R. PANEL CHILLER | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
74 | 2026-04-30 | BOH ENG | L8 | OFT | R. LV-5 | YORK | 12,5 PK / R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
75 | 2026-04-30 | BOH ENG | L8 | OFT | R. LV-5 | YORK | 6 PK / R22 | [7 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | Unit Rusak
No | Date | Category | Floor | Area | Tenant | Merk | Capacity (PK) | Compressor Ampere | [9 empty] | Air Temperature (oC) | [5 empty] | Room Temperature |  |  | Air Flow (Ft/m) |  |  | Performa Unit (CFM) | Remarks
[8 empty] | Name Plate | Before |  |  | After |  |  | Margin |  |  | Supply |  | Margin | Return |  | Margin | (oC)
[9 empty] | R | S | T | R | S | T | R | S | T | Before | After |  | Before | After |  | Before | After | Margin | Before | After | Margin
1 |  | F&B | LB | PISC | ACAII | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
2 |  | F&B | LB | PISC | SALADSTOP! | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
3 |  | RETAIL | LB | PISC | GUDANG LOUIS VUITTON 001 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
4 |  | RETAIL | LB | PISC | GUDANG LOUIS VUITTON 002 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
5 |  | RETAIL | LB | PISC | GUDANG LOUIS VUITTON 003 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
6 |  | RETAIL | P2 | PISC | MEISO | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
7 |  | BOH | P2 | PISC | KLINIK PLAZA INDONESIA 001 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
8 |  | BOH | P2 | PISC | KLINIK PLAZA INDONESIA 002 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
9 |  | BOH | P2 | PISC | R. CALL CENTER | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
10 |  | BOH | P2 | PISC | LOBBY LIFT 15-16 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
11 |  | BOH | P2 | PISC | OFFICE SECURE PARKING (R. ADMIN) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
12 |  | BOH | P2 | PISC | OFFICE SECURE PARKING (R. PAK BAGJA) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
13 |  | BOH | P2 | PISC | OFFICE SECURE PARKING OPS 001 (R. CCTV) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
14 |  | BOH | P2 | PISC | OFFICE SECURE PARKING OPS 002 (R. MAINTENANCE) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
15 |  | BOH | P2 | PISC | OFFICE SECURE PARKING 001 (R. SERVER) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
16 |  | BOH | P2 | PISC | OFFICE SECURE PARKING 002 (R. SERVER) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
17 |  | BOH | P2 | PISC | POS SECURITY LOADING 001 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
18 |  | BOH | P2 | PISC | POS SECURITY LOADING 002 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
19 |  | BOH | P2 | PISC | R. PROVOST 001 (CCTV 1) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
20 |  | BOH | P2 | PISC | R. PROVOST 002 (CCTV 2) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
21 |  | BOH | P2 | PISC | R. PROVOST 003 (SERVER) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
22 |  | BOH | P2 | PISC | R. PROVOST 004 (DEPAN/RUANG KACA) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
23 |  | BOH | P2 | PISC | R. PROVOST 005 (INTEROGASI/TENGAH) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
24 |  | BOH | P2 | PISC | R. PROVOST (LOCKER) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
25 |  | BOH | P2 | PISC | R. MESIN LIFT 1-2 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
26 |  | BOH | P2 | PISC | R. MESIN LIFT 1-2 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
27 |  | BOH | P2 | PISC | R. IT SERVER K 14 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
28 |  | BOH | P2 | PISC | R. BUILDING MAINTENANCE | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
29 |  | BOH | P2 | PISC | TRASHROOM 001 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
30 |  | BOH | P2 | PISC | TRASHROOM 002 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
31 |  | BOH | P2 | PISC | TRASHROOM 003 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
32 |  | BOH ENG | L48 | OFT | R. TRAFO LV-7 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
33 |  | BOH ENG | L48 | OFT | R. TRAFO LV-7 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
34 |  | BOH ENG | L48 | OFT | R. PANEL LV-7 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
35 |  | BOH ENG | L48 | OFT | R. PANEL LV-7 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
36 |  | BOH | P2 | PISC | MASJID BAITURRAHMAN 009 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
37 |  | BOH | P2 | PISC | MASJID BAITURRAHMAN 010 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
38 |  | BOH | P2 | PISC | MASJID BAITURRAHMAN 011 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
39 |  | BOH | P2 | PISC | CORRIDOR LIFT 7-8 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
40 |  | BOH | P2 | PISC | R. CSO PRIA | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
41 |  | BOH | P2 | PISC | R. CSO WANITA | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
42 |  | BOH | P2 | PISC | LOCKER MINIAPOLIS PRIA | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
43 |  | BOH | P2 | PIE | LOCKER MINIAPOLIS WANITA | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
44 |  | BOH | P2 | PIE | TOILET CSO WANITA | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
45 |  | BOH | P2 | PIE | TOILET CSO PRIA | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
46 |  | BOH | P2 | PIE | OFFICE SECURITY PT. AMAN | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
47 |  | BOH | P2 | PIE | OFFICE GHP | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
48 |  | BOH | P2 | PIE | R. BKO | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
49 |  | BOH | P2 | PIE | LOCKER SECURITY NIGHT GUARD 001 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
50 |  | BOH | P2 | PIE | LOCKER SECURITY NIGHT GUARD 002 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
51 |  | BOH | P2 | PIE | KANTINA 001 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
52 |  | BOH | P2 | PIE | KANTINA 002 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
53 |  | BOH | P2 | PIE | KANTINA 003 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
54 |  | SALON | P2 | PIE | PAXI PLUS | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
55 |  | BOH | P2 | PIE | R. MITSUBISHI | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
56 | 2026-05-01 | BOH | P3 | PIE | LOCKER GHP PRIA | PANASONIC | 2 PK / R32 |  | 3.3 |  |  | 3 |  |  | -0.3 |  |  | 26.1 | 17.4 | -8.7 |  |  | 0 | 26.3 | 24.1 | -2.2 | 315.2 | 589 | 273.8
57 | 2026-05-01 | BOH | P3 | PIE | LOCKER GHP WANITA | PANASONIC | 2 PK / R32 |  | 4.1 |  |  | 4 |  |  | -0.1 |  |  | 18.5 | 17.4 | -1.1 |  |  | 0 | 21.1 | 21 | -0.1 | 350.6 | 529.9 | 179.3
58 |  | RETAIL | P3 | PISC | COLOR WASH | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
59 |  | BOH | P3 | PISC | R. DRIVER TENGAH | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
60 |  | BOH | P3 | PISC | GUDANG LOGISTIK 001 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
61 |  | BOH | P3 | PISC | GUDANG LOGISTIK 002 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
62 |  | BOH | P3 | PISC | JNE | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
63 |  | BOH | P3 | PISC | LOCKER KORLAP SECURE PARKING | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
64 |  | BOH | P3 | PISC | OFFICE SECURE PARKING (R. OPERATION) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
65 |  | BOH | P3 | PISC | OFFICE SECURE PARKING (R. SECURITY K-9) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
66 |  | BOH | P3 | PISC | OFFICE SECURE PARKING (EX. LOCKER WANITA) | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
67 |  | BOH | P3 | PISC | OFFICE KING VALET | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
68 |  | BOH | P3 | PISC | R. DRIVER K05 N | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
69 |  | BOH | P3 | PISC | R. DRIVER W18 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
70 |  | BOH | P3 | PISC | AEON | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
71 |  | BOH ENG | P3 | PISC | R. PANEL STP | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
72 |  | BOH ENG | P3 | PISC | R. PANEL STP | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
73 |  | BOH ENG | P3 | PISC | R. LAB BIOSANT | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
74 |  | BOH ENG | P3 | PISC | R. PANEL POMPA SW | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
75 |  | BOH ENG | P3 | PISC | R. PANEL POMPA SW | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
76 |  | BOH | P3 | PISC | R. MESIN LIFT 7 - 8 | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
77 |  | BOH | P4 | PIE | LOBBY LIFT CP | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
78 |  | BOH | P4 | PIE | KOPERASI PATEN | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
79 |  | BOH | P4 | PIE | KOPERASI PATEN | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
80 |  | BOH | P4 | PIE | R. KETUA KOPERASI PATEN | [9 empty] | 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0