## Report Plaza Indonesia
NO | Day Audit | Date | No Unit | Kategori | Lantai | Merk | Tahun | Type Unit | Area | (EAT) Entering Coil DB Temp. (°C) | (RH) Entering Air Humidity (%) | (LAT) Leaving Coil DB Temp. (°C) | (RH) Leaving Air Humidity (%) | ΔT (EAT-LAT) | (H) Entering Air Enthalphy (Btu/Lb) | (H) Leaving Air Enthalpy (Btu/Lb) | ΔH (Btu/Lb) | Air Face velocity (m/s) | Face Area coil (m2) | Air Flow Rate design (CFM) | Air Flow Rate actual (CFM) | Total cooling capacity design (btuh) | Total cooling capacty actual (btuh) | Selisih capacity design vs actual (btuh) | Status | Cooling capacity design vs actual (btuh) % |  | Entering Water Temp. (°C) | Leaving Water Temp. (°C) | ΔT Water (°C) | Power input (KW) | Keterangan | Tindakan
[8 empty] | Parameter ideal |  | 24°C | 65 | 14°C | - | 10°C | - | - | 10 Btu/Lb | 2,5 m/s | - |  | As Design Airflow |  | As Design Capacity |  |  |  |  | 7 °C | 12 °C | 5°C
1 | Day 47 | 2026-05-04 | AHU 0-32-1 The colage University | AHU | L37 | YORK | 2006 | YDM 40X80 | LANTA 37 | 24.7 | 69.6 | 16.3 | 94.1 | 8.4 | 33.2245 | 26.5762 | 6.6483 | 2.3 | 3.048 | 16269.947 | 14854.1964 | 733579.7555 | 444397.9949 | 289181.7606 | Unit Overhaul | 60.58% |  | 10.6 | 16.9 | 6.3 |  | Jarak Pin coil 88/20cm, Isolasi pipa kondensasi, tidak ada pressure gauge, chilled water flowrate sangat jauh dari design
2 |  | 2026-05-04 | AHU L3-001 | FCU | L3 | DAIKIN | 2025 | DDM1619 | UNIQLO L3 | 21.9 | 66.5 | 14.2 | 78.6 | 7.7 | 29.0681 | 22.4124 | 6.6557 | 2.4 | 4.37 | 34000 | 22222.8134 | 710036.9633 | 665590.6225 | 44446.3408 | Unit Normal | 93.74% |  | 9.2 | 14.1 | 4.9
3 |  | 2026-05-04 | AHU L3-17 | FCU | L3 | YORK | 2008 | YDM 60X80 | UNIQLO L3 | 21.8 | 68.2 | 13.6 | 92.2 | 8.2 | 29.2587 | 23.267 | 5.9917 | 2.19 | 4.59 | 24834.007 | 21299.1936 | 1112311.6292 | 574278.6931 | 538032.9361 | Unit Replace | 51.63% | Prioritas 2 | 9.5 | 15 | 5.5 |  | Jarak Pin coil 88/20cm, Fin coil, support, interior unit, handel valve & asesoris korosi.
4 |  | 2026-05-04 | FCU Adelle 001 | FCU | L3 | DAIKIN | 2025 | DDB 60 | Adelle L3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.32 | 0.3825 | 2000 | 1880.2941 | 64000 | 0 | 64000 | Unit Normal | 0% |  | 0 | 0 | 0 |  | Unit baru, tdk ada motorized, filter kotor, belum ada ducting
5 |  | 2026-05-04 | FCU Adelle 002 | FCU | L3 | DAIKIN | 2025 | DDB 60 | Adelle L3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.39 | 0.3825 | 2000 | 1937.0271 | 64000 | 0 | 64000 | Unit Normal | 0% |  | 0 | 0 | 0 |  | Unit baru, tdk ada motorized, filter kotor, belum ada ducting
6 |  | 2026-05-04 | FCU Coach | FCU | L2 | MCQUAY | 2005 | MCC 50 | Coach L2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 0 | 50000 | Unit Replace | 0% | Prioritas 1 | 0 | 0 | 0 |  | Unit tidak bisa running, bodi unit karat, drain pan karat, coil rusak, kabel berantakan
7 | Day 48 | 2026-05-05 | Ex Eichhol 001 | FCU | L3 | TRANE | 2009 | HCCA 18 | Ex Eichhol L3 | 26.4 | 56.2 | 16.4 | 81.1 | 10 | 32.355 | 25.0239 | 7.3311 | 1.06 | 0.35 | 1900 | 786.1045 | 57000 | 25933.6143 | 31066.3857 | Unit Replace | 45.5% | Prioritas 1 | 8.9 | 13.7 | 4.8 |  | Fin coil rusak, bodi unit karat, valve berlumut, drain karat
8 |  | 2026-05-05 | Ex Eichhol 002 | FCU | L3 | TRANE | 2009 | HCCA 18 | Ex Eichhol L3 | 26.1 | 56.3 | 17.4 | 65.9 | 8.7 | 32.0089 | 24.0674 | 7.9415 | 1.25 | 0.35 | 1900 | 927.01 | 57000 | 33128.3323 | 23871.6677 | Unit Replace | 58.12% | Prioritas 2 | 9.2 | 15.2 | 6 |  | Fin coil rusak, bodi unit karat, valve berlumut, drain karat
9 |  | 2026-05-05 | Ex Eichhol 003 | FCU | L3 | TRANE | 2009 | HCCA 18 | Ex Eichhol L3 | 21.4 | 67 | 14.5 | 94 | 6.9 | 28.5712 | 24.4598 | 4.1114 | 1.5 | 0.35 | 1900 | 1112.412 | 57000 | 20580.9822 | 36419.0178 | Unit Replace | 36.11% | Prioritas 1 | 8.9 | 13.3 | 4.4 |  | Fin coil rusak, bodi unit karat, valve berlumut, drain karat
10 |  | 2026-05-05 | LVYSaint Laurent | FCU | L1 | DAIKIN | 2025 | DDB 60 | Saint Laurent LT.1 | 22.4 | 64.8 | 15.2 | 85.6 | 7.2 | 29.3438 | 24.2623 | 5.0815 | 2.44 | 0.4725 | 2000 | 2442.8568 | 60000 | 55860.3547 | 4139.6453 | Unit Normal | 93.1% |  | 8.8 | 13.3 | 4.5 |  | Unit baru, tdk ada motorized, tidak ducting external
11 |  | 2026-05-05 | Masimo Dutti 001 | FCU | L1 | DAIKIN | 2025 | DDB 50 | Masimo Dutti L1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1703.3333 | 0 | 51100 | 0 | 51100 | Unit Normal | 0% |  | 0 | 0 | 0 |  | Tidak ada motorized, flexible return sobek, tdiak ada drain pan external
12 |  | 2026-05-05 | Masimo Dutti 002 | FCU | L1 | DAIKIN | 2025 | DDB 50 | Masimo Dutti L1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1703.3333 | 0 | 51100 | 0 | 51100 | Unit Normal | 0% |  | 0 | 0 | 0 |  | Tidak ada motorized, tdiak ada drain pan external
13 |  | 2026-05-05 | Masimo Dutti 007 | FCU | L1 | TRANE | 2008 | HCCA 10 | Masimo Dutti L1 | 22.8 | 66.3 | 13.8 | 77.4 | 9 | 30.1097 | 21.8847 | 8.225 | 0.86 | 0.35 | 1135.592 | 637.7829 | 37000 | 23606.0013 | 13393.9987 | Unit Replace | 63.8% | Prioritas 2 | 9.5 | 13.2 | 3.7 |  | Fin coil rusak, bodi unit karat, drain pan karat, kabel berantakan, isolasi conden
14 |  | 2026-05-05 | Masimo Dutti 010 | FCU | L1 | MCQUAY | 2008 | MCC 40 | Masimo Dutti L1 | 26.8 | 58.2 | 17.8 | 77.6 | 9 | 33.348 | 26.1143 | 7.2336 | 1.2 | 0.315 | 1333.3333 | 800.9366 | 40000 | 26071.554 | 13928.446 | Unit Replace | 65.18% | Prioritas 2 | 8.9 | 13.5 | 4.6 |  | Coil rusak, bodi unit karat & kabel berantakan
15 |  | 2026-05-05 | Masimo Dutti 011 | FCU | L1 | YORK | 2016 | YCC 60 C | Masimo Dutti L1 | 29.7 | 53.7 | 19.8 | 73.2 | 9.9 | 35.9599 | 27.7477 | 8.2122 | 1.37 | 0.39 | 2500 | 1132.1176 | 60000 | 41837.1854 | 18162.8146 | Unit Overhaul | 69.73% |  | 8.9 | 13.4 | 4.5 |  | Kabel di box panel berantakan & isolasi konden
16 |  | 2026-05-05 | Masimo Dutti 012 | FCU | L1 | YORK | 2016 | YSB 60 BA | Masimo Dutti L1 | 26.8 | 58.2 | 17 | 77.5 |  | 33.348 | 25.2119 | 8.1361 | 1.04 | 0.4455 | 2500 | 981.7195 | 60000 | 35943.0257 | 24056.9743 | Unit Overhaul | 59.91% |  | 9.3 | 15.2 | 5.9 |  | Trdapat Coil yg rebah, kabel berantakan
17 | Day 49 | 2026-05-06 | Masimo Dutti 003 | FCU | L1 | TRANE | 2006 | HCCA 18 | Masimo Dutti L1 | 23.8 | 63.8 | 14.1 | 86.2 | 9.7 | 30.8351 | 23.1497 | 7.6854 | 1.1 | 0.4 | 1900 | 932.3072 | 57000 | 32243.2601 | 24756.7399 | Unit Replace | 56.57% | Prioritas 2 | 9.6 | 13.6 | 4 |  | Fin coil rusak, bodi unit karat, drain karat, main ducting supply rusak
18 |  | 2026-05-06 | Masimo Dutti 004 | FCU | L1 | TRANE | 2006 | HCCA 14 | Masimo Dutti L1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900 | 0 | 57000 | 0 | 57000 | Unit Overhaul | 0% |  | 0 | 0 | 0 |  | Manhole unit di kompon tidak bisa di buka
19 |  | 2026-05-06 | Masimo Dutti 005 | FCU | L1 | TRANE | 2006 | HCCA 14 | Masimo Dutti L1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1371.192 | 0 | 47000 | 0 | 47000 | Unit Replace | 0% | Prioritas 1 | 0 | 0 | 0 |  | Fin coil rusak, bodi unit karat, drain karat, isolasi conden, unit tidak bisa running
20 |  | 2026-05-06 | Masimo Dutti 006 | FCU | L1 | TRANE | 2006 | HCCA 14 | Masimo Dutti L1 | 22.3 | 64.7 | 14.2 | 81.7 | 8.1 | 29.2071 | 22.756 | 6.4511 | 1.12 | 0.35 | 1371.192 | 830.601 | 47000 | 24112.3264 | 22887.6736 | Unit Replace | 51.3% | Prioritas 2 | 8.9 | 13.5 | 4.6 |  | Fin coil rusak, bodi unit karat, drain karat, handel valve korosi
21 |  | 2026-05-06 | Masimo Dutti 008 | FCU | L1 | TRANE | 2008 | HCCA 10 | Masimo Dutti L1 | 24.2 | 71.2 | 16.9 | 88.2 | 7.3 | 32.8944 | 26.5239 | 6.3705 | 1.12 | 0.35 | 1135.592 | 830.601 | 37000 | 23810.9722 | 13189.0278 | Unit Replace | 64.35% | Prioritas 2 | 9.6 | 15.6 | 6 |  | Fin coil rusak banyak yg rebah, bodi unit karat, drain pan karat
22 |  | 2026-05-06 | Masimo Dutti 009 | FCU | L1 | MCQUAY | 2008 | MCC 40 | Masimo Dutti L1 | 21.1 | 72 | 15.1 | 79.9 | 6 | 29.0916 | 23.4816 | 5.61 | 1.4 | 0.315 | 1333.3333 | 934.4261 | 40000 | 23589.7106 | 16410.2894 | Unit Replace | 58.97% | Prioritas 2 | 8.9 | 13.5 | 4.6 |  | Coil rusak, bodi unit karat & kabel berantakan
23 |  | 2026-05-06 | Aigner 001 | FCU | L2 | TRANE | 2006 | HCCA 18 | Aigner L2 | 24.2 | 62.9 | 14.2 | 86.9 | 10 | 31.1409 | 23.3331 | 7.8078 | 1.09 | 0.4 | 1900 | 923.8317 | 57000 | 32458.7648 | 24541.2352 | Unit Replace | 56.95% | Prioritas 2 | 8.9 | 13.2 | 4.3 |  | Coil rusak, bodi unit karat & motorized valve belum di konek
24 |  | 2026-05-06 | Aigner 002 | FCU | L2 | MCQUAY | 2005 | MCC 60 | Aigner L2 | 29.3 | 50.2 | 20.8 | 76.2 | 8.5 | 34.4197 | 29.4478 | 4.9719 | 1.56 | 0.4725 | 3380 | 1561.8264 | 60000 | 34943.7736 | 25056.2264 | Unit Replace | 58.24% | Prioritas 2 | 14.5 | 18.3 | 3.8 |  | bodi unit karat, coil rusak, tempreature chilledwater tidak sesuai kemungkinan ada sumbatann di strainer
25 |  | 2026-05-06 | Pilar 001 | FCU | L3 | DAIKIN | 2025 | DDB 50 | Pilar 001 L3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1703.3333 | 0 | 51100 | 0 | 51100 | Unit Normal | 0% |  | 0 | 0 | 0 |  | Bakdrain external unit air menggenang, bersihkan jalur drain
26 |  | 2026-05-06 | Pilar 002 | FCU | L3 | DAIKIN | 2025 | DDB 60 | Pilar 001 L3 | 21.1 | 67.2 | 14.6 | 84 | 6.5 | 28.258 | 23.4312 | 4.8268 | 2.42 | 0.5 | 2600 | 2563.8448 | 60000 | 55688.5902 | 4311.4098 | Unit Normal | 92.81% |  | 8.8 | 13.8 | 5 |  | Motorized valve belum di konek
27 |  | 2026-05-06 | Pilar 003 | FCU | L3 | DAIKIN | 2025 | DDB 50 | Pilar 001 L3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1703.3333 | 0 | 51100 | 0 | 51100 | Unit Normal | 0% |  | 0 | 0 | 0 |  | Motorized valve belum di konek
28 |  | 2026-05-06 | Pilar 004 | FCU | L3 | DAIKIN | 2025 | DDB 50 | Pilar 001 L3 | 21.5 | 67.9 | 14.4 | 87.5 | 7.1 | 28.8482 | 23.6143 | 5.2339 | 2.3 | 0.425 | 1703.3333 | 2071.2052 | 51100 | 48782.0636 | 2317.9364 | Unit Normal | 95.46% |  | 8.9 | 13.8 | 4.9 |  | Motorized valve belum di konek
29 | Day 50 | 2026-05-07 | Alo 001 | FCU | L2 | YORK | 2023 | MAC 60 CW | Alo L2 | 21.2 | 71.5 | 15.5 | 81 | 5.7 | 29.1253 | 24.035 | 5.0902 | 2.32 | 0.48 | 2500 | 2359.5848 | 60000 | 54048.6315 | 5951.3685 | Unit Normal | 90.08% |  | 8.9 | 13.9 | 5
30 |  | 2026-05-07 | Alo 002 | FCU | L2 | YORK | 2023 | SBH 60 BW | Alo L2 | 22.4 | 67.4 | 16 | 84.1 | 6.4 | 29.8336 | 24.9613 | 4.8723 | 2.35 | 0.48 | 2500 | 2390.0966 | 60000 | 52403.7273 | 7596.2727 | Unit Normal | 87.34% |  | 9.6 | 14.7 | 5.1
31 |  | 2026-05-07 | Alo 003 | FCU | L2 | MCQUAY | 2022 | MCC 60 | Alo L2 | 24.7 | 72.2 | 17.8 | 90.5 | 6.9 | 33.7927 | 27.9336 | 5.8591 | 2.2 | 0.455 | 3380 | 2120.9989 | 60000 | 55922.0128 | 4077.9872 | Unit Normal | 93.2% |  | 9.3 | 15.5 | 6.2 |  | Terdapat coil yg rebah, bok panel unit tidak ada cover
32 |  | 2026-05-07 | Alo 004 | FCU | L2 | MCQUAY | 2022 | MCC 60 | Alo L2 | 23.1 | 67.8 | 16.3 | 85.9 | 6.8 | 30.7725 | 25.5267 | 5.2458 | 1.05 | 0.455 | 3380 | 1012.2949 | 60000 | 23896.5493 | 36103.4507 | Unit Replace | 39.83% | Prioritas 1 | 9.3 | 14.6 | 5.3 |  | Coil banyak yg rebah
33 |  | 2026-05-07 | Alo 005 | FCU | L2 | YORK | 2023 | SBH 60 BW | Alo L2 | 24.2 | 76.7 | 18.4 | 89.5 | 5.8 | 34.0612 | 28.5435 | 5.5178 | 2.3 | 0.48 | 2500 | 2339.2435 | 60000 | 58083.1599 | 1916.8401 | Unit Normal | 96.81% |  | 9.7 | 15.7 | 6
34 |  | 2026-05-07 | Alo 006 | FCU | L2 | MCQUAY | 2022 | MCC 60 | Alo L2 | 23.9 | 63.4 | 16 | 80.6 | 7.9 | 30.8755 | 24.5234 | 6.3521 | 1.53 | 0.455 | 3380 | 1475.0583 | 60000 | 42163.8551 | 17836.1449 | Unit Overhaul | 70.27% |  | 8.9 | 13.7 | 4.8 |  | Coil banyak yg rebah
35 |  | 2026-05-07 | DORE | FCU | L3 | DAIKIN | 2007 | MCC 50 | DORE L3 | 23.6 | 67.9 | 18.5 | 80.7 | 5.1 | 31.4233 | 27.3702 | 4.0531 | 1.1 | 0.455 | 2410.3625 | 1060.4994 | 50000 | 19342.3135 | 30657.6865 | Unit Replace | 38.68% | Prioritas 1 | 10.5 | 15.4 | 4.9 |  | Coil rusak, bodi unit karat & kabel berantakan
36 |  | 2026-05-07 | JOE MALONE | AHU | L2 | DAIKIN | 2025 | DDB 115 BW | JOE MALONE LT.2 | 22.5 | 70.8 | 15.8 | 75.7 | 6.7 | 30.6008 | 23.7036 | 6.8972 | 2.43 | 0.6825 | 3531 | 3514.1095 | 116021 | 109068.5934 | 6952.4066 | Unit Normal | 94.01% |  | 10.5 | 15.4 | 4.9 |  | Motorized valve belum di konek
37 |  | 2026-05-07 | DIPTYQUE | AHU | L2 | DAIKIN | 2025 | DDB 115 BW | JOE MALONE LT.2 | 22.5 | 70.8 | 14.5 | 88.1 | 8 | 30.6008 | 23.7902 | 6.8106 | 2.43 | 0.6825 | 3531 | 3514.1095 | 116021 | 107698.8968 | 8322.1032 | Unit Normal | 92.83% |  | 9.1 | 14.6 | 5.5 |  | Motorized valve belum di konek
38 | Day 51 | 2026-05-08 | Alo 007 | FCU | L2 | MCQUAY | 2008 | MCC 40 | Alo L2 | 23.9 | 65.6 | 18.7 | 70.9 | 5.2 | 31.3309 | 26.1472 | 5.1837 | 1.65 | 0.315 | 1333.3333 | 1101.2879 | 40000 | 25689.1869 | 14310.8131 | Unit Replace | 64.22% | Prioritas 2 | 8.9 | 14.8 | 5.9 |  | Coil banyak yg rebah
39 |  | 2026-05-08 | Alo 008 | FCU | L2 | MCQUAY | 2008 | MCC 40 | Alo L2 | 23.2 | 76.8 | 16.7 | 76.2 | 6.5 | 32.6879 | 24.7152 | 7.9727 | 1.31 | 0.27 | 1333.3333 | 749.4479 | 40000 | 26888.022 | 13111.978 | Unit Replace | 67.22% | Prioritas 2 | 8.9 | 14.8 | 5.9 |  | Coil banyak yg rebah
40 |  | 2026-05-08 | Alo 009 | FCU | L2 | MCQUAY | 2008 | SBH 40 | Alo L2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1333.3333 | 0 | 40000 | 0 | 40000 | Unit Overhaul | 0% |  | 0 | 0 | 0 |  | Unit tidak bisa running kemngukinan thermostat rusak
41 |  | 2026-05-08 | Berlutti 001 | FCU | L1 | DAIKIN | 2022 | DDB 75 BW | Berlutti LT.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2540 | 0 | 76200 | 0 | 76200 | Unit Normal | 100% |  | 0 | 0 | 0 |  | Unit baru, drain tidk ngalir
42 |  | 2026-05-08 | Berlutti 002 | FCU | L1 | DAIKIN | 2025 | DDB 60 | Berlutti LT.1 | 23.8 | 72.2 | 17.2 | 89.2 | 6.6 | 32.5664 | 27.0172 | 5.5492 | 2.35 | 0.4725 | 2600 | 2352.7514 | 60000 | 58751.1686 | 1248.8314 | Unit Normal | 97.92% |  | 9.2 | 15.3 | 6.1 |  | Unit baru, tidak ada motorized valve
43 |  | 2026-05-08 | Berlutti 003 | FCU | L1 | YORK | 2024 | YCW 1200 | Berlutti LT.1 | 23.4 | 77.3 | 17.9 | 88.5 | 5.5 | 33.0635 | 27.774 | 5.2895 | 2.3 | 0.385 | 1371.192 | 1876.2682 | 47000 | 44660.0752 | 2339.9248 | Unit Normal | 95.02% |  | 9.6 | 14.3 | 4.7 |  | Unit baru, tidak ada motorized valve
44 |  | 2026-05-08 | FCU Le Comtoir 001 | FCU | L1 | DAIKIN | 2025 | DDB 100 | Le Comtoir LT.1 | 27.1 | 67.6 | 18.1 | 91.6 | 9 | 36.1106 | 28.4686 | 7.642 | 2.38 | 0.585 | 3000 | 2950.1166 | 106500 | 101451.5925 | 5048.4075 | Unit Normal | 95.26% |  | 9.3 | 14.4 | 5.1 |  | Unit baru, tidak ada motorized valve
45 |  | 2026-05-08 | FCU Le Comtoir 002 | FCU | L1 | DAIKIN | 2016 | DDB 60 | Le Comtoir LT.1 | 29.5 | 59.3 | 18.5 | 91 | 11 | 37.322 | 28.8924 | 8.4296 | 1.35 | 0.4 | 2600 | 1144.1952 | 60000 | 43402.7349 | 16597.2651 | Unit Replace | 72.34% | Prioritas 2 | 9.4 | 15.4 | 6 |  | Coil, support coil & drain korosi, isolasi pipa kondensasi
46 |  | 2026-05-08 | FCU Le Comtoir 003 | FCU | L1 | DAIKIN | 2016 | DDB 100 | Le Comtoir LT.1 | 28.1 | 63 | 27.9 | 63.8 | 0.2 | 36.3491 | 36.2768 | 0.072323 | 1.5 | 0.54 | 3000 | 1716.2928 | 106500 | 558.5732 | 105941.4268 | Unit Replace | 0.5245% | Prioritas 1 | 15 | 25.1 | 10.1 |  | Coil & support coil korosi, chilled water tersumbat
47 |  | 2026-05-08 | FCU Le Comtoir 004 | FCU | L1 | DAIKIN | 2016 | DDB 60 | Le Comtoir LT.1 | 30.4 | 64.3 | 19.9 | 90.7 | 10.5 | 40.1872 | 30.6937 | 9.4935 | 1.1 | 0.4 | 2600 | 932.3072 | 60000 | 39828.8062 | 20171.1938 | Unit Replace | 66.38% | Prioritas 2 | 9.4 | 15.4 | 6 |  | Coil, support coil & drain korosi, isolasi pipa kondensasi, interior unit sangat kotor
48 |  | 2026-05-08 | AHU Le Comtoir 005 | AHU | L1 | DAIKIN | 2025 | DDB 115 BW | Le Comtoir LT.1 | 28.9 | 71.7 | 20.8 | 86.8 | 8.1 | 39.9747 | 31.2641 | 8.7105 | 2.38 | 0.585 | 3000 | 2950.1166 | 116000 | 115636.9552 | 363.0448 | Unit Normal | 99.69% |  | 9.6 | 15.3 | 5.7 |  | Unit masih bagus, filter kotor
49 |  | 2026-05-08 | FCU Le Comtoir 006 | FCU | L1 | DAIKIN | 2016 | DDB 60 | Le Comtoir LT.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2600 | 0 | 60000 | 0 | 60000 | Unit Overhaul | 0% |  | 0 | 0 | 0 |  | Unit tidak bisa di audit belum ada manhole untuk ke unit
50 |  | 2026-05-08 | FCU Le Comtoir 007 | FCU | L1 | TRANE | 2004 | HCCA 24 | Le Comtoir LT.1 | 28.1 | 63 | 27.9 | 63.8 | 0.2 | 36.3491 | 36.2768 | 0.072323 | 1.5 | 0.54 | 2521.509 | 1716.2928 | 72000 | 558.5732 | 71441.4268 | Unit Replace | 0.7758% | Prioritas 1 | 9.6 | 15.3 | 5.7 |  | Airvan di pipa coil outlet unit rusak sehingga valve chws & chwr harus di tutup
51 | Day 52 | 2026-05-11 | FCU NEW BALANCE 001 | FCU | L2 | TRANE | 2008 | HCCA 24 | NEW BALANCE LT.2 | 22.6 | 72.6 | 17.4 | 90.2 | 5.2 | 31.0714 | 27.3973 | 3.6741 | 2.15 | 0.5425 | 2521.509 | 2471.4087 | 72000 | 40860.9359 | 31139.0641 | Unit Overhaul | 56.75% |  | 8.8 | 13.1 | 4.3 |  | Unit noice, bodi unit kotor & sedikit korosi di bagian sisi coil | Cek bearing fan & lakukan cleaning secara berkala
52 |  | 2026-05-11 | FCU NEW BALANCE 002 | FCU | L2 | TRANE | 2008 | HCCA 18 | NEW BALANCE LT.2 | 22.7 | 77.2 | 12 | 89.1 | 10.7 | 32.0877 | 21.2896 | 10.7982 | 1.05 | 0.27 | 1900 | 600.7025 | 57000 | 29189.1522 | 27810.8478 | Unit Replace | 51.21% | Prioritas 2 | 8.6 | 11.8 | 3.2 |  | Coil rusak, bodi unit korosi
53 |  | 2026-05-11 | FCU RADO 001 | FCU | L2 | MCQUAY | 2006 | MCW 1200 | RADO LT.2 | 21.6 | 76.6 | 18.1 | 81.6 | 3.5 | 30.5288 | 27.0287 | 3.5001 | 1.8 | 0.3875 | 1135.592 | 1477.9188 | 36500 | 23277.8974 | 13222.1026 | Unit Replace | 63.78% | Prioritas 2 | 9.1 | 13.1 | 4 |  | Coil masih cukup bagus hanya sudah banyak terjadi korosi di bodi & support unit
54 |  | 2026-05-11 | FCU UNDER ARMOUR 001 | FCU | L2 | TRANE | 2009 | HCCA 24 | UNDER ARMOUR LT.2 | 23.7 | 69.8 | 16.1 | 91.6 |  | 31.9403 | 26.0192 | 5.9211 | 1.8 | 0.465 | 2521.509 | 1773.5026 | 72000 | 47254.9764 | 24745.0236 | Unit Overhaul | 65.63% |  | 9.8 | 13.6 |  |  | Coil masih cukup bagus hanya sudah banyak terjadi korosi di bodi & support unit
55 |  | 2026-05-11 | FCU UNDER ARMOUR 002 | FCU | L2 | TRANE | 2009 | HCCA 24 | UNDER ARMOUR LT.2 | 21.3 | 73.7 | 12.3 | 89.4 | 9 | 29.6339 | 21.6206 | 8.0133 | 1.35 | 0.48 | 2521.509 | 1373.0342 | 72000 | 49511.1242 | 22488.8758 | Unit Overhaul | 68.77% |  | 9.5 | 12 | 2.5 |  | Coil masih cukup bagus hanya sudah banyak terjadi korosi di bodi & support unit | Bersihkan fincoil & lakukan pengecatan
56 |  | 2026-05-11 | FCU UNDER ARMOUR 003 | FCU | L2 | TRANE | 2009 | HCCA 24 | UNDER ARMOUR LT.2 | 23.8 | 64.3 | 16.2 | 92.2 |  | 30.9379 | 26.2136 | 4.7242 | 1.58 | 0.48 | 2521.509 | 1606.9586 | 72000 | 34162.4964 | 37837.5036 | Unit Replace | 47.45% |  | 9.6 | 13.8 |  |  | Coil masih cukup bagus hanya sudah banyak terjadi korosi di bodi & support unit
57 |  | 2026-05-11 | FCU D'ORSAY | FCU | L3 | DAIKIN | 2025 | DDB 50 | D'ORSAY L3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1703.3333 | 0 | 51100 | 0 | 51100 | Unit Normal | 0% |  | 0 | 0 | 0 |  | Unit baru tidak ada bak drain external, tidak ada motorized valve
58 |  | 2026-05-11 | FCU BAHAGIA 001 | FCU | L3 | DAIKIN | 2025 | DDB 40 BW | BAHA GIA LT.3 | 25.5 | 67.7 | 16.3 | 90 | 9.2 | 33.8852 | 26.051 | 7.8341 | 2.07 | 0.24 | 1250 | 1052.6596 | 37300 | 37110.0036 | 189.9964 | Unit Normal | 99.49% |  | 8.8 | 14.2 | 5.4 |  | Unit baru , tidak ada filter, MV belum di konek
59 |  | 2026-05-11 | FCU BAHAGIA 002 | FCU | L3 | DAIKIN | 2025 | DDB 40 BW | BAHA GIA LT.3 | 25 | 65.5 | 16.7 | 85.4 | 8.3 | 32.7206 | 25.9202 | 6.8005 | 2.03 | 0.24 | 1250 | 1032.3183 | 37300 | 31591.0535 | 5708.9465 | Unit Normal | 84.69% |  | 8.8 | 14.3 | 5.5 |  | Unit baru , coil kotor, tidak ada filter, MV belum di konek
60 |  | 2026-05-11 | FCU BAHAGIA 003 | FCU | L3 | MCQUAY | 2008 | MCC 40 | BAHA GIA LT.3 | 25.2 | 70.5 | 16.6 | 87.1 | 8.6 | 34.1089 | 26.0269 | 8.0821 | 1.5 | 0.24 | 1500 | 762.7968 | 49000 | 27742.3508 | 21257.6492 | Unit Replace | 56.62% | Prioritas 2 | 9 | 14.5 | 5.5 |  | Bodi unit, fin coil & bak drain korosi, isolasi rusak
61 | Day 53 | 2026-05-12 | FCU BIMBI 001 | FCU | L3 | DAIKIN | 2025 | DDB 50 | BIMBI L3 | 26.8 | 74.1 | 17.4 | 95.8 | 9.4 | 37.2992 | 28.1692 | 9.13 | 2.35 | 0.24 | 1500 | 1195.0483 | 51100 | 49098.5947 | 2001.4053 | Unit Normal | 96.08% |  | 9.6 | 15.7 | 6.1 |  | Tidak ada MV
62 |  | 2026-05-12 | FCU BIMBI 002 | FCU | L3 | AICOOL | 2022 | FC 24 B | BIMBI L3 | 24.7 | 66.3 | 15.6 | 79.9 | 9.1 | 32.5046 | 24.0081 | 8.4965 | 0.9 | 0.16 | 800 | 305.1187 | 24000 | 11666.0351 | 12333.9649 | Unit Replace | 48.61% | Prioritas 1 | 9.1 | 14.4 | 5.3 |  | Bodi unit, fin coil & bak drain korosi
63 |  | 2026-05-12 | FCU BIMBI 003 | FCU | L3 | DAIKIN | 2025 | DDB 60 | BIMBI L3 | 24.8 | 63.7 | 17.6 | 91.2 | 7.2 | 32.0656 | 27.7829 | 4.2828 | 2.4 | 0.5625 | 2600 | 2860.488 | 60000 | 55128.4665 | 4871.5335 | Unit Normal | 91.88% |  | 9.4 | 15.1 | 5.7 |  | Tidak ada MV, bakdrain kotor
64 |  | 2026-05-12 | FCU PETIT BETEAU 001 | FCU | L3 | TRANE | 2009 | HCCA 14 | PETIT BETEAU L3 | 23.8 | 83.5 | 15.4 | 93.4 | 8.4 | 34.9091 | 25.4215 | 9.4875 | 1 | 0.35 | 1371.192 | 741.608 | 47000 | 31662.1499 | 15337.8501 | Unit Replace | 67.37% | Prioritas 2 | 9.2 | 14.6 | 5.4 |  | Fin coil rusak, bodi unit karat, pipa korosi
65 |  | 2026-05-12 | FCU PETIT BETEAU 002 | FCU | L3 | TRANE | 2009 | HCCA 18 | PETIT BETEAU L3 | 23.6 | 76.2 | 16 | 86.1 | 7.6 | 33.1165 | 25.2118 | 7.9048 | 1.05 | 0.385 | 1900 | 856.5572 | 57000 | 30469.0074 | 26530.9926 | Unit Replace | 53.45% | Prioritas 2 | 9.1 | 14.5 | 5.4 |  | Coil rusak, bodi unit korosi, isolasi rusak
66 |  | 2026-05-12 | FCU TEVA 001 | FCU | L2 | TRANE | 2009 | HCCA 18 | TEVA L2 | 23.4 | 71 | 20.4 | 80.7 | 3 | 31.793 | 29.7047 | 2.0883 | 1.5 | 0.385 | 1900 | 1223.6532 | 57000 | 11498.9354 | 45501.0646 | Unit Replace | 20.17% | Prioritas 1 | 9.1 | 20.2 | 11.1 |  | Coil rebah, bodi unit korosi, valve hanya ada di pipa chws, chilled water tersumbat & unit noice
67 |  | 2026-05-12 | FCU KINTARO SUSHI 001 | FCU | LB | TRANE | 2006 | HCCA 24 | KINTARO SUSH LB | 23.2 | 70.7 | 17.5 | 87.9 | 5.7 | 31.4735 | 27.2014 | 4.2721 | 1.8 | 0.48 | 2521.509 | 1830.7123 | 72000 | 35194.6265 | 36805.3735 | Unit Replace | 48.88% | Prioritas 1 | 9 | 15.4 | 6.4 |  | Coil rusak, bodi unit korosi, handel valve berjamur
68 |  | 2026-05-12 | FCU KINTARO SUSHI 002 | FCU | LB | TRANE | 2006 | HCCA 24 | KINTARO SUSH LB | 24.5 | 70.7 | 16 | 94 | 8.5 | 33.1927 | 26.2029 | 6.9899 | 1.1 | 0.48 | 2521.509 | 1118.7686 | 72000 | 35190.1639 | 36809.8361 | Unit Replace | 48.88% | Prioritas 1 | 8.8 | 13.8 | 5 |  | Coil rusak, bodi unit korosi, handel valve berjamur
69 |  | 2026-05-12 | FCU KINTARO SUSHI 003 | FCU | LB | TRANE | 2006 | HCCA 24 | KINTARO SUSH LB | 24.4 | 63.6 | 17.6 | 84.5 | 6.8 | 31.5384 | 26.8489 | 4.6895 | 1.6 | 0.48 | 2521.509 | 1627.2998 | 72000 | 34340.3088 | 37659.6912 | Unit Replace | 47.69% | Prioritas 1 | 8.9 | 13.6 | 4.7 |  | Coil rusak, bodi unit korosi, handel valve berjamur
70 |  | 2026-05-12 | FCU KINTARO SUSHI 004 | FCU | LB | TRANE | 2025 | FWW1800TF | KINTARO SUSH LB | 24.5 | 64.5 | 18.4 | 74.7 | 6.1 | 31.8574 | 26.374 | 5.4834 | 2.4 | 0.4725 | 2600 | 2402.8099 | 60000 | 59290.3007 | 709.6993 | Unit Normal | 98.82% |  | 8.9 | 13.6 | 4.7 |  | Unit baru,tidak ada MV, belum ada ducting suppy & return
71 | Day 54 | 2026-05-13 | FCU BALLY 001 | FCU | L2 | DAIKIN | 2026 | DDB 50 | BALLY LT.2 | 22.4 | 66.9 | 14.1 | 83.8 | 8.3 | 29.7393 | 22.885 | 6.8543 | 2.4 | 0.3025 | 1500 | 1538.3069 | 51100 | 47448.3004 | 3651.6996 | Unit Normal | 92.85% |  | 8.9 | 13.4 | 4.5
72 |  | 2026-05-13 | FCU BALLY 002 | FCU | L2 | YORK | 2024 | MAC 100 W | BALLY LT.2 | 24.6 | 61.2 | 16.6 | 82.6 | 8 | 31.2717 | 25.4404 | 5.8312 | 2.13 | 0.5625 | 3200 | 2538.6831 | 100000 | 66616.1652 | 33383.8348 | Unit Overhaul | 66.62% |  | 9.1 | 14.4 | 5.3 |  | Coil rusak
73 |  | 2026-05-13 | FCU BALLY 003 | FCU | L2 | DAIKIN | 2026 | DDB 50 | BALLY LT.2 | 21.6 | 67.7 | 14.7 | 87.5 | 6.9 | 28.9306 | 23.939 | 4.9916 | 2.34 | 0.425 | 1500 | 2107.2262 | 51100 | 47333.0488 | 3766.9512 | Unit Normal | 92.63% |  | 8.9 | 13.8 | 4.9 |  | Tidak ada motorized valve & bak drain tambahan
74 |  | 2026-05-13 | FCU BALLY 004 | FCU | L2 | DAIKIN | 2026 | DDB 50 | BALLY LT.2 | 23.2 | 67.3 | 15.6 | 91.9 | 7.6 | 30.7985 | 25.4717 | 5.3268 | 2.35 | 0.425 | 1500 | 2116.2314 | 51100 | 50727.2787 | 372.7213 | Unit Normal | 99.27% |  | 9.5 | 14.3 | 4.8 |  | Tidak ada motorized valve & bak drain tambahan
75 |  | 2026-05-13 | FCU BAHAGIA 002 | FCU | L2 | DAIKIN | 2026 | DDB 40 BW | BALLY LT.2 | 21.8 | 67.4 | 14.5 | 89.2 | 7.3 | 29.1135 | 23.9149 | 5.1985 | 2.34 | 0.2925 | 1250 | 1450.2674 | 37300 | 33926.7656 | 3373.2344 | Unit Normal | 90.96% |  | 8.9 | 13.9 | 5 |  | Unit baru , coil kotor, tidak ada MV, bakdrain external
76 |  | 2026-05-13 | FCU SK-11 | FCU | L2 | DAIKIN | 2025 | DDB 75 BW | BALLY LT.2 | 22.2 | 69.9 | 15.4 | 82.5 | 6.8 | 30.0575 | 24.1088 | 5.9487 | 2.46 | 0.54 | 3000 | 2814.7202 | 75000 | 75347.5187 | -347.5187 | Unit Normal | 100.5% |  | 9.3 | 14.5 | 5.2 |  | Unit baru , Tdak ada bakdrain externa
77 |  | 2026-05-13 | FCU CONVERSE 001 | FCU | L2 | TRANE | 2009 | HCCA 18 | CONVERSE L2 | 21.8 | 71.7 | 14.6 | 90.2 | 7.2 | 29.8945 | 24.1387 | 5.7558 | 1.64 | 0.385 | 1889.9946 | 1337.8608 | 57000 | 34652.2365 | 22347.7635 | Unit Normal | 60.79% |  | 8.9 | 13.8 | 4.9 |  | Coil masih cukup bagus, bodi unit, bakdrain korosi
78 |  | 2026-05-13 | FCU CONVERSE 002 | FCU | L2 | TRANE | 2009 | HCCA 18 | CONVERSE L2 | 21.7 | 71 | 15.7 | 90 | 6 | 29.6446 | 25.3542 | 4.2904 | 2.33 | 0.385 | 1889.9946 | 1900.7413 | 57000 | 36696.9974 | 20303.0026 | Unit Replace | 64.38% | Prioritas 2 | 9.3 | 14.3 | 5 |  | Coil masih cukup bagus, bodi unit, bakdrain korosi, unit noice dari ducting
79 |  | 2026-05-13 | FCU GOLF HOUSE 001 | FCU | L2 | TRANE | 2009 | HCCA 24 | GOLF HOUSE LT.2 | 21.4 | 70.6 | 14.8 | 88.1 | 6.6 | 29.2083 | 24.1174 | 5.0909 | 1.2 | 0.7425 | 2521.509 | 1887.9221 | 72000 | 43250.4287 | 28749.5713 | Unit Replace | 60.07% | Prioritas 2 | 8.9 | 13.6 | 4.7 |  | Coil masih cukup bagus hanya sudah banyak terjadi korosi di bodi & support unit, pipa chws & chwr kondensasi
80 |  | 2026-05-13 | FCU GOLF HOUSE 002 | FCU | L2 | TRANE | 2008 | HCCA 10 | GOLF HOUSE LT.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1135.592 | 0 | 37000 | 0 | 37000 | Unit Overhaul | 0% |  | 0 | 0 | 0 |  | Unit tidak bisa running thermostat rusak, bodi unit korosi
81 |  | 2026-05-13 | FCU GOLF HOUSE 003 | FCU | L2 | MCQUAY | 2009 | MCC 60 | GOLF HOUSE LT.2 | 22.5 | 68.2 | 15.9 | 85.3 | 6.6 | 30.1069 | 24.9995 | 5.1074 | 1.45 | 0.4725 | 3380 | 1451.6977 | 60000 | 33364.7779 | 26635.2221 | Unit Replace | 55.61% | Prioritas 2 | 9.1 | 14.3 | 5.2 |  | Fincoil rusak, bodi unit banyak korosi & unit noice
82 | Day 55 | 2026-05-15 | CORK & SCREW 001 | FCU | L1 | YORK | 2018 | SBH 125 BW | CORK & SCREW L1 | 25.9 | 75.3 | 18.1 | 91.6 | 7.8 | 36.2271 | 28.4686 | 7.7584 | 1.25 | 0.84 | 4600 | 2224.824 | 125000 | 77675.3351 | 47324.6649 | Unit Overhaul | 62.14% |  | 9 | 13.4 | 4.4 |  | Fincoil korosi, drain korosi, valve berjamur, isolasi kondensasi | Ganti coil, perbaiki isolai, bersihkan ataw ganti handel valve
83 |  | 2026-05-15 | CORK & SCREW 002 | AHU | L1 | YORK | 2018 | SBH 125 BW | CORK & SCREW L1 | 26.7 | 60 | 20.1 | 86.7 | 6.6 | 33.6618 | 30.3085 | 3.3533 | 1.7 | 0.9375 | 4600 | 3376.965 | 125000 | 50957.9443 | 74042.0557 | Unit Replace | 40.77% | Prioritas 1 | 9.6 | 15.6 | 6 |  | Fincoil korosi, drain korosi, valve berjamur, isolasi kondensasi
84 |  | 2026-05-15 | CORK & SCREW 003 | AHU | L1 | YORK | 2018 | SBH 125 BW | CORK & SCREW L1 | 26.7 | 60 | 17.8 | 89.1 | 8.9 | 33.6618 | 27.7357 | 5.9261 | 1.38 | 0.9375 | 4600 | 2741.301 | 125000 | 73103.1483 | 51896.8517 | Unit Replace | 58.48% | Prioritas 2 | 9.1 | 14.5 | 5.4 |  | Fincoil korosi, drain korosi, valve berjamur, isolasi kondensasi
85 |  | 2026-05-15 | OSTERIA GIA 001 | AHU | L1 | YORK | 2016 | SBH 100 DW | OSTERIA GIA L1 | 28.3 | 61.7 | 18.1 | 94.5 | 10.2 | 36.2825 | 28.8873 | 7.3952 | 1.766 | 0.513 | 3200 | 1919.6163 | 100000 | 63881.7025 | 36118.2975 | Unit Overhaul | 63.88% |  | 9.2 | 15.3 | 6.1 |  | Fin coil kotor, valve korosi, pipa drain tidak ada isolasi
86 |  | 2026-05-15 | OSTERIA GIA 002 | AHU | L1 | YORK | 2016 | SBH 100 DW | OSTERIA GIA L1 | 29.4 | 70.8 | 19.9 | 83.2 | 9.5 | 40.5317 | 29.4784 | 11.0533 | 1.195 | 0.513 | 3200 | 1298.9476 | 100000 | 64609.4618 | 35390.5382 | Unit Overhaul | 64.61% |  | 9.7 | 15.8 | 6.1 |  | Fin coil kotor, valve korosi, pipa drain tidak ada isolasi & flexible ducting lepas
87 |  | 2026-05-15 | OSTERIA GIA 002 | AHU | L1 | YORK | 2016 | SBH 100 DW | OSTERIA GIA L1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3200 | 0 | 100000 | 0 | 100000 | Unit Overhaul | 0% |  | 0 | 0 | 0 |  | Unit tidak bisa du ukur karna akses di bawah kompor
88 |  | 2026-05-15 | SOME DIM SUM 001 | FCU | LB | TRANE | 0 | HCCA 10 | SOME DIM SUM LB | 24.2 | 62 | 15.6 | 71.2 | 8.6 | 30.9513 | 22.9508 | 8.0005 | 0.61 | 0.36 | 1135.592 | 465.306 | 37000 | 16752.0469 | 20247.9531 | Unit Replace | 45.28% | Prioritas 1 | 8.9 | 13.5 | 4.6 |  | Fin coil rusak banyak yg rebah, bodi unit karat, drain pan karat
89 |  | 2026-05-15 | SOME DIM SUM 002 | FCU | LB | YORK | 2022 | YSB 48 WDS | SOME DIM SUM LB | 25.5 | 65.5 | 18.4 | 77 | 7.1 | 33.3809 | 26.7103 | 6.6707 | 1.27 | 0.405 | 1597.726 | 1089.8459 | 48000 | 32715.0099 | 15284.9901 | Unit Overhaul | 68.16% |  | 9.5 | 15.3 | 5.8 |  | Unit masih cukup bagus, tidak ada bakdrain external | Lakukan cleaning secara maksimal
90 |  | 2026-05-15 | IKKUDO ICHI 001 | FCU | LB | DAIKIN | 2025 | FWW1800TF | IKKUDO ICHI LB | 23.5 | 73.1 | 16.8 | 88.5 | 6.7 | 32.3493 | 26.4453 | 5.904 | 2.34 | 0.4375 | 2600 | 2169.2034 | 60000 | 57631.6257 | 2368.3743 | Unit Normal | 96.05% |  | 9 | 14.3 | 5.3 |  | Unit baru,tidak ada MV, belum ada ducting suppy & return
91 |  | 2026-05-15 | IKKUDO ICHI 002 | FCU | LB | DAIKIN | 2025 | FWW1800TF | IKKUDO ICHI LB | 23.3 | 73 | 15.9 | 91.1 | 7.4 | 32.0631 | 25.7219 | 6.3412 | 2.25 | 0.4375 | 2600 | 2085.7725 | 60000 | 59518.5975 | 481.4025 | Unit Normal | 99.2% |  | 9.1 | 14.4 | 5.3 |  | Unit baru,tidak ada MV, belum ada ducting suppy & return
92 | Day 56 | 2026-05-18 | FCU HUBLOT 001 | FCU | L1 | DAIKIN | 2024 | DDB 50 | HUBLOT 001 LT.1 | 24.2 | 77.4 | 17.5 | 86.8 | 6.7 | 34.21 | 27.0491 | 7.1609 | 2.5 | 0.27 | 1500 | 1430.244 | 51100 | 46088.3421 | 5011.6579 | Unit Normal | 90.19% |  | 9 | 15.2 | 6.2 |  | Tidak ada motorized valve & bak drain tambahan, filter, drain unit kotor
93 |  | 2026-05-18 | FCU HUBLOT 002 | FCU | L1 | YORK | 2023 | MAC 60 | HUBLOT 001 LT.1 | 23.6 | 71 | 18.1 | 82.9 | 5.5 | 32.0548 | 27.2155 | 4.8393 | 2.36 | 0.5 | 2500 | 2500.2784 | 60000 | 54447.6814 | 5552.3186 | Unit Normal | 90.75% |  | 8.9 | 15.3 | 6.4 |  | tdak ada MV, tidak ada bak drain external, coil, drain & filter kotor
94 |  | 2026-05-18 | AHU BAAN MENSI 001 | AHU | L1 | DAIKIN | 2025 | DDB 115 BW | BAAN MENSI LT.1 | 25.9 | 64.9 | 17.2 | 84.3 | 8.7 | 33.7772 | 26.3523 | 7.4249 | 2.47 | 0.6075 | 3000 | 3179.4324 | 116000 | 106231.7154 | 9768.2846 | Unit Normal | 91.58% |  | 9.2 | 15.6 | 6.4 |  | Unit masih bagus, filter kotor, coil kotor
95 |  | 2026-05-18 | AHU BAAN MENSI 002 | AHU | L1 | DAIKIN | 2025 | DDB 100 | BAAN MENSI LT.1 | 25.4 | 61.4 | 15 | 89.6 | 10.4 | 32.316 | 24.5135 | 7.8025 | 2.34 | 0.585 | 3000 | 2900.5348 | 106500 | 101841.3101 | 4658.6899 | Unit Normal | 95.63% |  | 8.9 | 14.7 | 5.8 |  | Unit masih bagus, filter kotor, coil kotor
96 |  | 2026-05-18 | FCU OSIM 001 | FCU | L3 | MCQUAY | 2006 | MCC 60 | OSIM LT.3 | 21.8 | 63.6 | 15.8 | 81.5 | 6 | 28.4247 | 24.4186 | 4.0061 | 1.6 | 0.4725 | 3380 | 1601.8733 | 59000 | 28877.7593 | 30122.2407 | Unit Replace | 48.95% | Prioritas 1 | 9.4 | 25.5 | 16.1 |  | Fincoil rusak, bodi unit banyak korosi, kabel brantakan & pipa drain tidak di isolasi
97 |  | 2026-05-18 | FCU OSIM 002 | FCU | L3 | MCQUAY | 2006 | MCC 60 | OSIM LT.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3380 | 0 | 59000 | 0 | 59000 | Unit Replace | 0% | Prioritas 1 | 0 | 0 | 0 |  | Unit tidak bisa running motor short, bodi unit banyak korosi, kabel brantakan & pipa drain tidak di isolasi
98 |  | 2026-05-18 | FCU OSIM 003 | FCU | L3 | MCQUAY | 2006 | MCC 60 | OSIM LT.3 | 21.3 | 66.8 | 16.7 | 76.6 | 4.6 | 28.4197 | 24.7675 | 3.6522 | 1.7 | 0.4725 | 3380 | 1701.9904 | 59000 | 27972.3437 | 31027.6563 | Unit Replace | 47.41% | Prioritas 1 | 9.1 | 15.3 | 6.2 |  | Fincoil rusak, bodi unit banyak korosi, kabel brantakan & pipa drain tidak di isolasi
99 |  | 2026-05-18 | FCU MASSHIRO&CO 001 | FCU | L3 | MCQUAY | 2006 | MCC 20 | OSIM LT.3 | 22.9 | 70 | 17.3 | 83.6 | 5.6 | 30.952 | 26.3733 | 4.5787 | 1.45 | 0.175 | 3380 | 537.6658 | 20000 | 11078.2285 | 8921.7715 | Unit Replace | 55.39% |  | 9 | 14.5 | 5.5 |  | Fincoil rusak, bodi unit banyak korosi, kabel brantakan
100 |  | 2026-05-18 | FCU MASSHIRO&CO 001 | FCU | L3 | MCQUAY | 2006 | MCC 20 | OSIM LT.3 | 23.4 | 67.5 | 17.4 | 83.7 | 6 | 31.0891 | 26.5034 | 4.5857 | 1.35 | 0.175 | 3380 | 500.5854 | 20000 | 10329.9945 | 9670.0055 | Unit Replace | 51.65% |  | 9 | 14.5 | 5.5 |  | Fincoil rusak, bodi unit banyak korosi, kabel brantakan, valve berjamur
101 | Day 57 | 2026-05-19 | AHU BAAN MENSI 003 | AHU | L1 | DAIKIN | 2025 | DDB 115 BW | BAAN MENSI LT.1 | 24.9 | 67.2 | 16.1 | 92.1 | 8.8 | 32.9652 | 26.0824 | 6.8829 | 2.43 | 0.675 | 3531 | 3475.4929 | 115000 | 107646.0241 | 7353.9759 | Unit Normal | 93.61% |  | 9.2 | 15.6 | 6.4 |  | Unit masih bagus, tdk ada bakdrain external& ada sumbatan chilled water
102 |  | 2026-05-19 | AHU BAAN MENSI 004 | AHU | L1 | DAIKIN | 2025 | DDB 100 BW | BAAN MENSI LT.1 | 24.9 | 67.2 | 15.8 | 86.2 | 9.1 | 32.9652 | 24.9992 | 7.966 | 2.4 | 0.54 | 3000 | 2746.0685 | 100000 | 98438.8127 | 1561.1873 | Unit Normal | 98.44% |  | 8.9 | 14.6 | 5.7 |  | Unit masih bagus, tdk ada bakdrain external& ada sumbatan chilled water
103 |  | 2026-05-19 | FCU CHOPARD 001 | FCU | L1 | DAIKIN | 2025 | DDB 50 BW | LT.1 CHOPARD | 23 | 75.2 | 14.4 | 95.7 | 8.6 | 32.1004 | 24.5389 | 7.5615 | 2.34 | 0.2925 | 1500 | 1450.2674 | 51100 | 49347.878 | 1752.122 | Unit Normal | 96.57% |  | 9.2 | 14.5 | 5.3 |  | Tida ada bakdrain external, tidak ada MV & handel valce condensasi
104 |  | 2026-05-19 | FCU CHOPARD 002 | FCU | L1 | DAIKIN | 2025 | DDB 60 | LT.1 CHOPARD | 21.5 | 73.8 | 14.9 | 95.1 | 6.6 | 29.9002 | 25.0436 | 4.8566 | 2.36 | 0.5 | 2500 | 2500.2784 | 60000 | 54642.3498 | 5357.6502 | Unit Normal | 91.07% |  | 8.8 | 13.8 | 5 |  | Tida ada bakdrain external, tidak ada MV & Main ducting supply bocor
105 |  | 2026-05-19 | FCU LENORE | FCU | L3 | DAIKIN | 2025 | DDB 50 BW | LT.3 LENORE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 0 | 51100 | 0 | 51100 | Unit Normal | 0% |  | 0 | 0 | 0 |  | unit baru, Pemipaan sudah terkonekasi denganbaik, ducting belum ada & power unit belum di sambung
106 |  | 2026-05-19 | FCU CALVIN KLEAN 001 | FCU | L3 | MCQUAY | 2006 | MCC 60 | LT.3 CALVIN KLEAN | 24 | 66.3 | 19 | 79.3 | 5 | 31.6028 | 27.7554 | 3.8474 | 1.3 | 0.4725 | 3380 | 1301.522 | 59000 | 22533.6819 | 36466.3181 | Unit Replace | 38.19% | Prioritas 1 | 8.9 | 15.4 | 6.5 |  | Coil rusak, kabel berantakan & pipa kondensasi
107 |  | 2026-05-19 | FCU CALVIN KLEAN 002 | FCU | L3 | MCQUAY | 2006 | MCC 50 | LT.3 CALVIN KLEAN | 23.4 | 63.6 | 17.5 | 77.7 | 5.9 | 30.3065 | 25.7918 | 4.5148 | 1.5 | 0.345 | 2400 | 1096.5204 | 50000 | 22277.4184 | 27722.5816 | Unit Replace | 44.55% | Prioritas 1 | 9.5 | 15.9 | 6.4 |  | Coil rusak, kabel berantakan & pipa kondensasi
108 |  | 2026-05-19 | FCU BILLSTONE | FCU | L3 | DAIKIN | 2025 | DDB 75 BW | LT.3 BILLSTONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0.5625 | 3000 | 2979.675 | 75000 | 0 | 75000 | Unit Normal | 0% |  | 0 | 0 | 0 |  | Unit baru tenant fitout, main falve belum di buka yg bisa di cek hanya dari air flownya saja
109 |  | 2026-05-19 | FCU HARLAN HOLDEN 001 | FCU | L3 | DAIKIN | 2025 | DDB 50 BW | LT.3 HARLAN HOLDEN | 22.4 | 68 | 14.5 | 85.6 | 7.9 | 29.9467 | 23.5068 | 6.4399 | 2.5 | 0.3 | 1500 | 1589.16 | 51100 | 46052.9645 | 5047.0355 | Unit Normal | 90.12% |  | 8.9 | 14.5 | 5.6 |  | Terdapat pipa yg kondensasi d bawah strrainer, MV belum di konek
110 |  | 2026-05-19 | FCU HARLAN HOLDEN 002 | FCU | L3 | DAIKIN | 2025 | DDB 50 BW | LT.3 HARLAN HOLDEN | 22.5 | 63.2 | 14.2 | 84.6 | 8.3 | 29.1592 | 23.0777 | 6.0815 | 2.15 | 0.48 | 2500 | 2186.6842 | 60000 | 59842.3002 | 157.6998 | Unit Normal | 99.74% |  | 8.9 | 13.4 | 4.5 |  | MV belum di konek & tidak ada bakdarin external
111 | Day 58 | 2026-05-20 | FCU ADIDAS 001 | FCU | L2 | TRANE | 2008 | HCCA 18 | LT.2 ADIDAS | 25.7 | 69.1 | 16.2 | 95.7 | 9.5 | 34.4844 | 26.6593 | 7.8251 | 1.186 | 0.315 | 1889.9946 | 791.5924 | 57000 | 27874.36 | 29125.64 | Unit Replace | 48.9% | Prioritas 1 | 8.9 | 13.6 | 4.7 |  | Tidak ada filter,pin coil sudah mulai rapuh,body unit mulai korosi,tidak ada ducting return.
112 |  | 2026-05-20 | FCU ADIDAS 002 | FCU | L2 | YORK | 2008 | MAC 60 DW | LT.2 ADIDAS | 25.8 | 67.7 | 17.5 | 90 | 8.3 | 34.2968 | 27.4923 | 6.8045 | 1.696 | 0.42 | 2500 | 1509.3206 | 60000 | 46215.7718 | 13784.2282 | Unit Overhaul | 77.03% |  | 9.2 | 15.5 | 6.3 |  | Filter kotor & tidak ada bakdrin external
113 |  | 2026-05-20 | FCU ADIDAS 003 | FCU | L2 | TRANE | 2006 | HCCA 14 | LT.2 ADIDAS | 24.6 | 65.8 | 16.7 | 89.4 | 7.9 | 32.2661 | 26.4454 | 5.8207 | 1.074 | 0.4 | 1371.192 | 910.2708 | 47000 | 23842.6643 | 23157.3357 | Unit Replace | 50.73% | Prioritas 2 | 9.6 | 15.1 | 5.5 |  | Fin coil sudah mulai rapuh,body unit mulai korosi,tidak ada aksesoris
114 |  | 2026-05-20 | FCU ADIDAS 004 | FCU | L2 | DAIKIN | 2025 | DDB 75 BW | LT.2 ADIDAS | 25.4 | 68.3 | 18.3 | 85 | 7.1 | 33.8857 | 27.7603 | 6.1254 | 2.34 | 0.54 | 3000 | 2677.4168 | 75000 | 73801.3886 | 1198.6114 | Unit Normal | 98.4% |  | 9.5 | 14.6 | 5.1 |  | Tidak ada filter dan bak drain external
115 |  | 2026-05-20 | FCU NEW ERA 001 | FCU | L2 | MCQUAY | 2009 | MCC 30 | LT.2 NEW ERA | 23 | 66.2 | 16.9 | 83.1 | 6.1 | 30.3345 | 25.8457 | 4.4888 | 1.16 | 0.255 | 1000 | 626.7647 | 30000 | 12660.3684 | 17339.6316 | Unit Replace | 42.2% | Prioritas 1 | 9.5 | 15.4 | 5.9 |  | Tidak ada filter,pin coil rusak, isolasi rusak.
116 |  | 2026-05-20 | FCU HERSCHEL SUPPLY COMPANY | FCU | L2 | TRANE | 2009 | HCCA 18 | LT.2 HERCHEL SUPPLY COMPANY | 24.1 | 66 | 15.2 | 93.8 |  | 31.6673 | 25.2373 | 6.43 | 1.25 | 0.385 | 1889.9946 | 1019.711 | 57000 | 29505.1313 | 27494.8687 | Unit Replace | 51.76% |  | 8.8 | 13.7 | 4.9 |  | Fin coil rusak & bodi unit sudah banyak korosi
117 |  | 2026-05-20 | FCU ELCHEMIST 001 (EX.MALINDA 002) | FCU | L3 | TRANE | 2007 | HCCA 18 | LT.3 ELCHEMIST (EX.MALINDA) | 21.5 | 71.7 | 13.7 | 95.9 | 7.8 | 29.5254 | 23.7735 | 5.7519 | 2.318 | 0.385 | 1889.9946 | 1890.9521 | 57000 | 48944.2721 | 8055.7279 | Unit Overhaul | 85.87% |  | 8.7 | 13 | 4.3 |  | Coil masih bagus tetapi bodi unit sudah mengalami banyak korosi
118 |  | 2026-05-20 | FCU SEBASTIAN RED 001 | FCU | L3 | TRANE | 2008 | HCCA 14 | LT.3 SEBASTIAN RED | 23.9 | 61.3 | 16.3 | 83.9 | 7.6 | 30.4414 | 25.2712 | 5.1702 | 1.16 | 0.285 | 1371.192 | 700.5017 | 47000 | 16297.9497 | 30702.0503 | Unit Replace | 34.68% | Prioritas 1 | 9.2 | 15.1 | 5.9 |  | Fin coil rusak & bodi unit sudah banyak korosi
119 |  | 2026-05-20 | FCU SEBASTIAN RED 002 | FCU | L3 | TRANE | 2008 | HCCA 18 | LT.3 SEBASTIAN RED | 22 | 75.2 | 14.2 | 84.5 | 7.8 | 30.7881 | 23.0666 | 7.7215 | 1.72 | 0.35 | 1889.9946 | 1275.5658 | 57000 | 44321.6766 | 12678.3234 | Unit Overhaul | 77.76% |  | 8.9 | 13 | 4.1 |  | Coil masih bagus tetapi bodi unit sudah mengalami banyak korosi
120 |  | 2026-05-20 | FCU BOSS KIDS 001 | FCU | L3 | TRANE | 2006 | HCCA 18 | LT.3 BOSS KIDS | 22.5 | 66.8 | 14.3 | 93 | 8.2 | 29.8413 | 24.1226 | 5.7187 | 1.972 | 0.4025 | 1889.9946 | 1681.8186 | 57000 | 43280.2705 | 13719.7295 | Unit Overhaul | 75.93% |  | 8.9 | 13.1 | 4.2 |  | Coil masih bagus tetapi bodi unit sudah mengalami banyak korosi & isolasi konden
121 | Day 59 | 2026-05-21 | FCU TAGHEUER 001 | FCU | L1 | DAIKIN | 2025 | DDB 50 BW | LT.1 TAGHEUER | 24.4 | 73.8 | 16.2 | 89.3 | 8.2 | 33.7228 | 25.8448 | 7.878 | 2.33 | 0.2925 | 1500 | 1444.0697 | 51100 | 51193.7644 | -93.7644 | Unit Normal | 100.2% |  | 9.3 | 15.1 | 5.8 |  | Tida ada bakdrain external, tidak ada MV
122 |  | 2026-05-21 | FCU RICHARD MILE 002 | FCU | L1 | TRANE | 2005 | HCCA 14 | LT .1 RICHARD MILE | 23.4 | 67.7 | 15.6 | 72.1 | 7.8 | 31.1293 | 23.06 | 8.0693 | 1 | 0.2975 | 1371.192 | 630.3668 | 47000 | 22889.7785 | 24110.2215 | Unit Replace | 48.7% | Prioritas 1 | 9.2 | 14.3 | 5.1 |  | Fin coil rusak & bodi unit sudah banyak korosi
123 |  | 2026-05-21 | FCU RICHARD MILE 001 | FCU | L1 | DAIKIN | 2025 | DDB 50 BW | LT.1 RICHARD MILE | 23.1 | 68.7 | 14.7 | 84.3 | 8.4 | 30.95 | 23.5715 | 7.3785 | 2.4 | 0.2925 | 1500 | 1487.4538 | 51100 | 49388.0577 | 1711.9423 | Unit Normal | 96.65% |  | 8.9 | 13.4 | 4.5 |  | Interior unit tidak bisa di cek karna manhole hanya ada di sisi return
124 |  | 2026-05-21 | FCU PLANET SPORT 004 | FCU | L2 | TRANE | 2009 | HCCA 18 | LT.2 PLANET SPORT | 24.2 | 62.3 | 14.5 | 96.4 | 9.7 | 31.0145 | 24.7326 | 6.2819 | 1.821 | 0.33 | 1889.9946 | 1273.2986 | 57000 | 35994.0479 | 21005.9521 | Unit Overhaul | 63.15% |  | 9 | 13.7 | 4.7 |  | Terdapat fin coil yg rebah & korosi di bodi unit
125 |  | 2026-05-21 | FCU PLANET SPORT 003 | FCU | L2 | TRANE | 2009 | HCCA 24 | LT.2 PLANET SPORT | 22.4 | 66.5 | 14.8 | 95.3 | 7.6 | 29.664 | 24.9515 | 4.7125 | 2.468 | 0.56 | 2521.509 | 2928.4617 | 72000 | 62101.6522 | 9898.3478 | Unit Overhaul | 86.25% |  | 9 | 13.5 | 4.5 |  | Fin coil kotor
126 |  | 2026-05-21 | FCU PLANET SPORT 001 | FCU | L2 | TRANE | 2009 | HCCA 24 | LT.2 PLANET SPORT | 23.8 | 66.3 | 16.2 | 87.6 | 7.6 | 31.3494 | 25.6288 | 5.7206 | 1.9 | 0.56 | 2521.509 | 2254.4883 | 72000 | 58036.8481 | 13963.1519 | Unit Overhaul | 80.61% |  | 9.4 | 15.3 | 5.9 |  | Fin col masih cukup bagus
127 |  | 2026-05-21 | FCU PLANET SPORT 002 | FCU | L2 | TRANE | 2009 | HCCA 24 | LT.2 PLANET SPORT | 22.2 | 66.1 | 14.5 | 95.1 | 7.7 | 29.35 | 24.5848 | 4.7651 | 2 | 0.56 | 2521.509 | 2373.1456 | 72000 | 50887.3362 | 21112.6638 | Unit Overhaul | 70.68% |  | 9.4 | 15.3 | 5.9 |  | Fin col masih cukup bagus
128 |  | 2026-05-21 | FCU KENZO KIDS 001 | FCU | L3 | TRANE | 2006 | HCCA 18 | LT.3 KENZO KIDS | 23 | 68 | 13.9 | 95.6 | 9.1 | 30.687 | 23.9638 | 6.7231 | 1.802 | 0.385 | 1889.9946 | 1470.0154 | 57000 | 44474.0789 | 12525.9211 | Unit Overhaul | 78.02% |  | 8.8 | 12.9 | 4.1 |  | Tidak ada filter,body unit mulai korosi.pin coil mulai rapuh,coil depan.
129 |  | 2026-05-21 | FCU TULOLA 001 | FCU | L3 | MCQUAY | 2006 | MCC 60 | LT.3 TULOLA | 25.4 | 58.3 | 18.7 | 73.8 | 6.7 | 31.613 | 26.5789 | 5.0341 | 1.22 | 0.35 | 3380 | 904.7618 | 59000 | 20495.9212 | 38504.0788 | Unit Replace | 34.74% | Prioritas 1 | 9.3 | 15.3 | 6 |  | Fin coil rusak & bodi unit sudah banyak korosi
130 |  | 2026-05-21 | FCU TULOLA 002 | FCU | L3 | TRANE | 2006 | HCCA 10 | LT.3 TULOLA | 25.9 | 53.4 | 19.2 | 73.2 | 6.7 | 31.0881 | 27.0553 | 4.0328 | 1.11 | 0.3 | 1135.592 | 705.587 | 37000 | 12804.7023 | 24195.2977 | Unit Replace | 34.61% | Prioritas 1 | 9.4 | 15.4 | 6 |  | Fin coil rusak & bodi unit sudah banyak korosi
131 | Day 60 | 2026-05-22 | FCU ZEGNA 001 | FCU | L1 | YORK | 0 | MAC 75 CW | ZEGNA LT.1 | 24.4 | 74.8 | 15.1 | 91.3 | 9.3 | 33.9377 | 24.8262 | 9.1116 | 2.05 | 0.39 | 2500 | 1694.0446 | 75000 | 69459.2434 | 5540.7566 | Unit Normal | 92.61% |  | 9 | 13.9 | 4.9 |  | Unit masih bagus, tidak ada MV & bakdrain external
132 |  | 2026-05-22 | FCU ZEGNA 002 | FCU | L1 | MCQUAY | 2006 | MCC 50 | ZEGNA LT.1 | 25.7 | 71.9 | 21.4 | 79.2 | 4.3 | 35.1359 | 30.735 | 4.4009 | 0.9 | 0.455 | 2400 | 867.6814 | 50000 | 17183.5593 | 32816.4407 | Unit Replace | 34.37% | Prioritas 1 | 9.5 | 15.4 | 5.9 |  | Coil rusak, kabel berantakan & pipa kondensasi
133 |  | 2026-05-22 | FCU ZEGNA 003 | FCU | L1 | MCQUAY | 2006 | MCC 50 | ZEGNA LT.1 | 25.3 | 67 | 20.5 | 85.3 | 4.8 | 33.4548 | 30.6058 | 2.8489 | 1.7 | 0.455 | 2400 | 1638.9537 | 50000 | 21011.7275 | 28988.2725 | Unit Replace | 42.02% | Prioritas 1 | 9.1 | 15.2 | 6.1 |  | Coil rusak, kabel berantakan & handel valve korosi
134 |  | 2026-05-22 | FCU ZEGNA 004 | FCU | L1 | MCQUAY | 2006 | MCC 50 | ZEGNA LT.1 | 25.8 | 71 | 20.7 | 84.2 | 5.1 | 35.0689 | 30.6849 | 4.3841 | 1.2 | 0.455 | 2400 | 1156.9085 | 50000 | 22823.8225 | 27176.1775 | Unit Replace | 45.65% | Prioritas 1 | 9.1 | 15.6 | 6.5 |  | Coil rusak, kabel berantakan & handel valve korosi
135 |  | 2026-05-22 | FCU ZEGNA 005 | FCU | L1 | MCQUAY | 2006 | MCC 50 | ZEGNA LT.1 | 26 | 69.7 | 20.2 | 84.1 | 5.8 | 35.0475 | 30.0117 | 5.0358 | 1.08 | 0.455 | 2400 | 1041.2176 | 50000 | 23595.2311 | 26404.7689 | Unit Replace | 47.19% | Prioritas 1 | 9.8 | 15.7 | 5.9 |  | Coil rusak, kabel berantakan, handel valve korosi & isolasi kondnen
136 |  | 2026-05-22 | FCU KIDS STATION 001 | FCU | L3 | TRANE | 2009 | HCCA 24 | LT.3 KIDS STATION | 25.3 | 61.3 | 13.4 | 92.9 | 11.9 | 32.1667 | 23.1255 | 9.0412 | 0.8 | 0.66 | 2521.509 | 1118.7686 | 72000 | 45517.6288 | 26482.3712 | Unit Overhaul | 63.22% |  | 9 | 13 | 4 |  | Fin coil karat, bodi unit masih cukup bagus
137 |  | 2026-05-22 | FCU KIDS STATION 002 | FCU | L3 | TRANE | 2009 | HCCA 24 | LT.3 KIDS STATION | 25.1 | 59.2 | 13 | 84.2 | 12.1 | 31.4474 | 21.8059 | 9.6415 | 0.577 | 0.66 | 2521.509 | 806.9119 | 72000 | 35009.292 | 36990.708 | Unit Replace | 48.62% | Prioritas 1 | 9 | 12.8 | 3.8 |  | Fin coil karat, bodi unit korosi
138 |  | 2026-05-22 | FCU WACOAL | FCU | L3 | MCQUAY | 2006 | MCC 40 | LT.3 WACOAL | 22.3 | 65.2 | 15.6 | 82.4 | 6.7 | 29.3006 | 24.3125 | 4.9882 | 1.79 | 0.27 | 1500 | 1024.0547 | 49000 | 22986.7302 | 26013.2698 | Unit Replace | 46.91% | Prioritas 1 | 9 | 13 | 4 |  | Fin coil rebah & bodi unit mulai karat
139 |  | 2026-05-22 | FCU KALAH TO COMVANY | FCU | L3 | TRANE | 2006 | HCCA 18 | LT.3 KALAH TO COMVANY | 23.6 | 66.2 | 11.2 | 91.6 | 12.4 | 31.0775 | 20.7265 | 10.3511 | 0.53 | 0.44 | 1889.9946 | 494.1228 | 57000 | 23016.1456 | 33983.8544 | Unit Replace | 40.38% | Prioritas 1 | 8.9 | 11 | 2.1 |  | koil rebah & bodi unit karat
140 |  | 2026-05-22 | FCU L'OCCITANE | FCU | L3 | MCQUAY | 2007 | MCC 60 | LT.3 L'OCCITANE | 24.3 | 64.3 | 17.4 | 79.3 | 6.9 | 31.5617 | 25.8996 | 5.6621 | 1.17 | 0.455 | 3380 | 1127.9858 | 59000 | 28740.3882 | 30259.6118 | Unit Replace | 48.71% | Prioritas 1 | 9.2 | 15.4 | 6.2 |  | koil rebah & bodi unit mulai korosi
141 | Day 61 | 2026-05-25 | FCU ADIDAS KIDS 001 | FCU | L3 | TRANE | 2009 | HCCA 18 | LT.3 ADIDAS KIDS 001 | 22 | 69.4 | 12.4 | 94.3 | 9.6 | 29.7195 | 22.2046 | 7.5149 | 0.93 | 0.44 | 1889.9946 | 867.0457 | 57000 | 29320.884 | 27679.116 | Unit Replace | 51.44% | Prioritas 2 | 8.9 | 11.1 | 2.2 |  | Coil masih cukup bagus hanya bodi unit sudah banyak korosi
142 |  | 2026-05-25 | FCU ADIDAS KIDS 002 | FCU | L3 | TRANE | 2009 | HCCA 14 | LT.3 ADIDAS KIDS 001 | 22.3 | 78.6 | 15.5 | 91.2 | 6.8 | 31.8168 | 25.271 | 6.5458 | 1.7 | 0.2975 | 1371.192 | 1071.6236 | 47000 | 31566.0241 | 15433.9759 | Unit Replace | 67.16% | Prioritas 2 | 9 | 14.5 | 5.5 |  | Coil masih cukup bagus hanya bodi unit sudah banyak korosi
143 |  | 2026-05-25 | FCU ADIDAS KIDS 003 | FCU | L3 | TRANE | 2009 | HCCA 18 | LT.3 ADIDAS KIDS 001 | 22 | 69.4 | 15.7 | 90.8 | 6.3 | 29.7195 | 25.4526 | 4.2669 | 1.3 | 0.44 | 1889.9946 | 1211.9994 | 57000 | 23271.8646 | 33728.1354 | Unit Replace | 40.83% | Prioritas 1 | 9.1 | 14.5 | 5.4 |  | Coil masih cukup bagus hanya bodi unit sudah banyak korosi
144 |  | 2026-05-25 | SHU GUO YIN XIANG 003 | FCU | L4 | MCQUAY | 2012 | MDB 75 BW | LT.4 SHU GUO YIN XIANG | 25.7 | 75.7 | 15.4 | 91.2 | 10.3 | 36.0221 | 25.1562 | 10.8659 | 0.8 | 0.54 | 4166.6667 | 915.3562 | 75000 | 44757.7843 | 30242.2157 | Unit Replace | 59.68% | Prioritas 2 | 9.5 | 14.8 | 5.3 |  | Coil korosi, MV tidak di konek, drain unit korosi
145 |  | 2026-05-25 | SHU GUO YIN XIANG 004 | FCU | L4 | MCQUAY | 2012 | MDB 75 BW | LT.4 SHU GUO YIN XIANG | 23.9 | 72.2 | 15.4 | 89.7 | 8.5 | 32.7006 | 24.9754 | 7.7252 | 1.24 | 0.54 | 4166.6667 | 1418.802 | 75000 | 49322.4932 | 25677.5068 | Unit Replace | 65.76% | Prioritas 2 | 9.4 | 14.6 | 5.2 |  | Coil korosi, MV tidak di konek, drain unit korosi & support coil korosi
146 |  | 2026-05-25 | SHU GUO YIN XIANG 005 | FCU | L4 | MCQUAY | 2012 | MDB 75 BW | LT.4 SHU GUO YIN XIANG | 24.9 | 69.6 | 16.4 | 87.1 | 8.5 | 33.4956 | 25.7952 | 7.7003 | 1.13 | 0.54 | 4166.6667 | 1292.9406 | 75000 | 44802.2664 | 30197.7336 | Unit Replace | 59.74% | Prioritas 2 | 9.5 | 15.1 | 5.6 |  | Coil rebah, MV tidak di konek, drain unit korosi & support coil korosi
147 |  | 2026-05-25 | SHU GUO YIN XIANG 007 | FCU | L4 | MCQUAY | 2012 | MCC 60 | LT.4 SHU GUO YIN XIANG | 24.6 | 68.4 | 18.4 | 81.4 | 6.2 | 32.8294 | 27.3544 | 5.475 | 1.2 | 0.455 | 3380 | 1156.9085 | 59000 | 28503.1782 | 30496.8218 | Unit Replace | 48.31% | Prioritas 1 | 9.6 | 15.4 | 5.8 |  | Coil rysak, MV tidak di konek, drain unit korosi & support coil korosi
148 |  | 2026-05-25 | SHU GUO YIN XIANG 008 | FCU | L4 | TRANE | 2012 | HCCA 10 | LT.4 SHU GUO YIN XIANG | 24.1 | 64.5 | 16.5 | 91.5 | 7.6 | 31.3527 | 26.4814 | 4.8714 | 2.1 | 0.3 | 1135.592 | 1334.8944 | 37000 | 29262.3603 | 7737.6397 | Unit Replace | 79.09% | Prioritas 2 | 9.3 | 15.8 | 6.5 |  | Fin coil masih cukup bagus tetapi bodi unit sudah banyak korosi
149 |  | 2026-05-25 | SHU GUO YIN XIANG 010 | FCU | L4 | TRANE | 2012 | HCCA 18 | LT.4 SHU GUO YIN XIANG | 24 | 63 | 16.4 | 81.1 |  | 30.9154 | 25.0239 | 5.8915 | 1.06 | 0.44 | 1889.9946 | 988.2456 | 57000 | 26200.3026 | 30799.6974 | Unit Replace | 45.97% | Prioritas 1 | 9.4 | 15.3 | 5.9 |  | Coil rusak & bodi unit korosi
150 |  | 2026-05-25 | FCU RELX | FCU | L4 | MCQUAY | 2012 | MCC 60 | LT.4 RELX | 23.3 | 70.3 | 17.4 | 82.3 | 5.9 | 31.5228 | 26.3112 | 5.2117 | 1.43 | 0.455 | 3380 | 1378.6493 | 59000 | 32332.6731 | 26667.3269 | Unit Replace | 54.8% | Prioritas 2 | 9.3 | 15.3 | 6 |  | Coil rysak, MV tidak di konek, kabel berantakan & support coil korosi
151 |  | 2026-05-25 | FCU DAY OFF | FCU | L4 | YORK | 2009 | SBH 50 | LT.4DAY OFF | 21.7 | 70.4 | 15.2 | 88.9 | 6.5 | 29.5362 | 24.6544 | 4.8819 | 2.2 | 0.28 | 1600 | 1305.2301 | 50000 | 28673.7894 | 21326.2106 | Unit Replace | 57.35% | Prioritas 2 | 8.9 | 14.5 | 5.6 |  | Fin coil rusak, bodi unit karat, support coil karat
152 | Day 62 | 2026-05-26 | FCU ARTKEA 01 | FCU | L4 | MCQUAY | 2012 | MCC 40 | LT.4 ARTKEA | 27.7 | 65.8 | 22.7 | 73 | 5 | 36.5167 | 31.2772 | 5.2394 | 1 | 0.27 | 1500 | 572.0976 | 49000 | 13488.6026 | 35511.3974 | Unit Replace | 27.53% | Prioritas 1 | 9.5 | 19 | 9.5 |  | Fin coil rusak, bodi unit mulai karat & chilled water tersumbat
153 |  | 2026-05-26 | FCU ARTKEA 02 | FCU | L4 | TRANE | 2012 | HCCA 18 | LT.4 ARTKEA | 25.2 | 61.6 | 17.3 | 80.8 | 7.9 | 32.1078 | 25.9915 | 6.1163 | 0.89 | 0.44 | 1889.9946 | 829.7534 | 57000 | 22837.5687 | 34162.4313 | Unit Replace | 40.07% | Prioritas 1 | 9.4 | 15.4 | 6 |  | Fin coil rebah, bodi unit karat, support coil karat
154 |  | 2026-05-26 | FCU ARTKEA 03 | FCU | L4 | MCQUAY | 2012 | MCC 60 | LT.4 ARTKEA | 25.8 | 72.3 | 20 | 81.6 | 5.8 | 35.3736 | 29.3458 | 6.0278 | 1.5 | 0.315 | 3380 | 1001.1708 | 60000 | 27156.8433 | 32843.1567 | Unit Replace | 45.26% | Prioritas 1 | 9.1 | 15.3 | 6.2 |  | Coil rusak & bodi unit korosi
155 |  | 2026-05-26 | FCU ARTKEA 05 | FCU | L4 | MCQUAY | 2012 | MCC 60 | LT.4 ARTKEA | 25.3 | 68.4 | 17.2 | 90.6 | 8.1 | 33.7719 | 27.2074 | 6.5644 | 1.74 | 0.4375 | 3380 | 1612.9974 | 60000 | 47647.9701 | 12352.0299 | Unit Normal | 79.41% |  | 9.6 | 15.7 | 6.1 |  | Coil & bodi unit masih cukup bagus
156 |  | 2026-05-26 | FCU ARTKEA 04 | FCU | L4 | YORK | 2016 | SBH 100 DW | LT.4 ARTKEA | 25.3 | 70.3 | 15.3 | 83.5 | 10 | 34.2027 | 24.1208 | 10.0819 | 1.27 | 0.54 | 3200 | 1453.1279 | 100000 | 65926.1032 | 34073.8968 | Unit Overhaul | 65.93% |  | 9 | 14.6 | 5.6 |  | Fin coil kotor, handel valve karat
157 |  | 2026-05-26 | SHU GUO YIN XIANG 001 | FCU | L4 | MCQUAY | 2012 | MDB 75 BW | LT.4 SHU GUO YIN XIANG | 25.9 | 72.9 | 19.9 | 80.5 | 6 | 35.6602 | 29.0419 | 6.6183 | 1.07 | 0.54 | 4166.6667 | 1224.2889 | 75000 | 36461.9966 | 38538.0034 | Unit Replace | 48.62% | Prioritas 1 | 9.2 | 15.2 | 6 |  | Coil rusak, MV tidak di konek, bodi unit korosi
158 |  | 2026-05-26 | SHU GUO YIN XIANG 002 | FCU | L4 | MCQUAY | 2012 | MDB 75 BW | LT.4 SHU GUO YIN XIANG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4166.6667 | 0 | 75000 | 0 | 75000 | Unit Replace | 0% | Prioritas 1 | 0 | 0 | 0 |  | Coil rusak, MV tidak di konek, bodi unit korosi & unit tidak bisa running
159 |  | 2026-05-26 | SHU GUO YIN XIANG 006 | FCU | L4 | MCQUAY | 2012 | MDB 75 BW | LT.4 SHU GUO YIN XIANG | 26.8 | 62.9 | 16.1 | 92.2 | 10.7 | 34.5113 | 26.095 | 8.4163 | 1.2 | 0.46 | 4166.6667 | 1169.6218 | 75000 | 44297.5478 | 30702.4522 | Unit Replace | 59.06% | Prioritas 2 | 9 | 13.7 | 4.7 |  | Coil rusak, MV tidak di konek, bodi unit korosi
160 |  | 2026-05-26 | SHU GUO YIN XIANG 011 | FCU | L4 | TRANE | 2012 | HCCA 10 | LT.4 SHU GUO YIN XIANG | 24.2 | 76.1 | 16.5 | 94.7 | 7.7 | 33.9337 | 26.8969 | 7.0368 | 1.45 | 0.27 | 1135.592 | 829.5415 | 37000 | 26267.9761 | 10732.0239 | Unit Overhaul | 70.99% |  | 8.8 | 13.9 | 5.1 |  | Fin coil masih cukup bagus tetapi bodi unit sudah banyak korosi
161 | Day 63 | 2026-05-29 | FCU EX MONDIAL 002 | FCU | L1 | DAIKIN | 2024 | DDB 60 | LT.1 EX MONDIAL | 23.8 | 68.2 | 17.1 | 84.4 | 6.7 | 31.7409 | 26.2496 | 5.4912 | 2.2 | 0.5 | 2500 | 2330.768 | 60000 | 57594.6654 | 2405.3346 | Unit Normal | 95.99% |  | 9.5 | 15.2 | 5.7 |  | Tidak ada MV, tidak ada bak drain external
162 |  | 2026-05-29 | FCU EX MONDIAL 001 | FCU | L1 | TRANE | 2007 | HCCA 24 | LT.1 EX MONDIAL | 23.2 | 67.5 | 16.9 | 85.2 | 6.3 | 30.8382 | 26.1248 | 4.7134 | 1.3 | 0.66 | 2521.509 | 1817.999 | 72000 | 38559.972 | 33440.028 | Unit Replace | 53.56% | Prioritas 2 | 9.1 | 15.1 | 6 |  | Fin coil rebah & bodi unit mulai karat
163 |  | 2026-05-29 | FCU EX MONDIAL 003 | FCU | L1 | MCQUAY | 2012 | MCC 60 | LT.1 EX MONDIAL | 23.9 | 68.3 | 18.2 | 83 | 5.7 | 31.8906 | 27.3491 | 4.5414 | 1.2 | 0.455 | 3380 | 1156.9085 | 59000 | 23643.0645 | 35356.9355 | Unit Replace | 40.07% | Prioritas 1 | 9.2 | 15.6 | 6.4 |  | Coil rusak, tidak ada MV & support coil korosi
164 |  | 2026-05-29 | FCU DE SALON 001 | FCU | L4 | DAIKIN | 2025 | DDB 60 | LT.4 DE SALON | 23.5 | 70.1 | 16.8 | 86.7 | 6.7 | 31.7413 | 26.2073 | 5.534 | 2.3 | 0.48 | 2500 | 2339.2435 | 60000 | 58254.2815 | 1745.7185 | Unit Normal | 97.09% |  | 9.5 | 15.2 | 5.7 |  | Tidak ada MV, tidak ada bak drain external & bodi unit kondensasi
165 |  | 2026-05-29 | FCU SAMWON GARDEN 01 | FCU | L4 | YORK | 2012 | MAC 60 | LT.4 SAMWON GARDEN | 26.1 | 71.5 | 17.9 | 84.8 | 8.2 | 35.6193 | 27.2482 | 8.3711 | 0.9 | 0.455 | 2500 | 867.6814 | 60000 | 32685.5473 | 27314.4527 | Unit Overhaul | 54.48% |  | 8.9 | 13.7 | 4.8 |  | Coil rusak, tidak ada MV, support coil korosi & pipa drain tidak di isolasi
166 |  | 2026-05-29 | FCU SAMWON GARDEN 03 | FCU | L4 | TRANE | 2012 | HCCA 24 | LT.4 SAMWON GARDEN | 25.3 | 71.2 | 16.9 | 93.1 | 8.4 | 34.4069 | 27.1767 | 7.2302 | 1.2 | 0.56 | 2521.509 | 1423.8874 | 72000 | 46327.5105 | 25672.4895 | Unit Replace | 64.34% | Prioritas 2 | 9 | 15.3 | 6.3 |  | Terdapat fin coil yg rebah & bodi unit sudah banyak korosi
167 |  | 2026-05-29 | FCU SAMWON GARDEN 04 | FCU | L4 | TRANE | 2012 | HCCA 18 | LT.4 SAMWON GARDEN | 25.6 | 71.8 | 13.2 | 92.9 | 12.4 | 34.9694 | 22.9107 | 12.0587 | 0.8 | 0.33 | 1889.9946 | 559.3843 | 57000 | 30354.6297 | 26645.3703 | Unit Overhaul | 53.25% |  | 8.9 | 12.2 | 3.3 |  | Fin coil masih cukup bagus tetapi bodi unit sudah banyak korosi