## Actual-AHU
No | Kode | Date | Area | Floor | AHU Unit |  |  |  | AMPERE (A) | [11 empty] | Air Temperature (oC) | [5 empty] | Room Temperature |  |  | Air Flow |  |  | Performa Unit | Remarks
[5 empty] | Code No | Merk | Type | Tenant / Supply To | Name Plate |  |  | Before |  |  | After |  |  | Margin |  |  | Supply |  | Margin | Return |  | Margin | (oC) |  |  | ( FT / M )
[9 empty] | Kw | Rpm | Amp | R | S | T | R | S | T | R | S | T | Before | After |  | Before | After |  | Before | After | Margin | Before | After | Margin
1 |  | 2026-05-25 | PIE | L.2 | AHU P2-08 | YORK | YDM 70 X 80 | CORRIDOR BROWN PUCK COFFEE | 3 | 1440 | 7.1 | 6.7 | 6.6 | 6.4 | 6.4 | 6.4 | 6.3 | 0.3 | 0.2 | 0.1 | 19.1 | 17 | 2.1 | 22.6 | 21.4 | 1.2 | 22.4 | 21.2 | 1.2 | 540 | 772 | 232 | 1598.04 | NORMAL
2 |  | 2026-05-25 | PISC | L3 | AHU L3-01 | YORK | YDM 50 X 80 | KIDS STATION | 15 | 1460 | 29.1 | 26.4 | 26.3 | 26.4 | 26.1 | 26.1 | 26 | 0.3 | 0.2 | 0.4 | 18.7 | 16.5 | 2.2 | 22.8 | 20.7 | 2.1 | 22.6 | 20.5 | 2.1 | 327 | 587 | 260 | 1215.09 | NORMAL
3 |  | 2026-05-03 | PISC | L3 | AHU L3-02 | YORK | YDM 40 X 70 | CORRIDOR MUSHOLLA WANITA SW | 7.5 | 1450 | 16.2 | 7.54 | 7.07 | 7.07 | 7 | 6.82 | 7 | 0.54 | 0.25 | 0.07 | 18.8 | 16.9 | 1.9 | 21.4 | 20 | 1.4 | 21.3 | 19.7 | 1.6 | 412.6 | 695.4 | 282.8 | 1439.478 | NORMAL
4 |  | 2026-05-03 | PISC | L3 | AHU L3-03 | YORK | YDM 40 X 50 | CORRIDOR ESCALATOR N | 7.5 | 1450 | 16.2 | 9 | 9.3 | 11.3 | 8.9 | 9.2 | 10.6 | 0.1 | 0.1 | 0.7 | 19.2 | 17.1 | 2.1 | 21.7 | 20.1 | 1.6 | 21.5 | 20 | 1.5 | 543.7 | 925.1 | 381.4 | 1914.957 | NORMAL
5 |  | 2026-05-05 | PISC | L3 | AHU L3-04 | TRANE | CLCP 60 | CORRIDOR JOHN FASHION | 11 | 1455 | 21.5 | 12.2 | 12.6 | 11.9 | 12.1 | 12.2 | 11.6 | 0.1 | 0.4 | 0.3 | 19.7 | 18.1 | 1.6 | 21.9 | 20.2 | 1.7 | 22 | 20.4 | 1.6 | 260 | 786 | 526 | 1627.02 | NORMAL
6 |  | 2026-05-06 | PISC | L3 | AHU L3-05 | TRANE | CLCP 60 | CORRIDOR WANDA JEWELLERY | 7.5 | 1450 | 16.2 | 14.64 | 15.23 | 15.11 | 13.64 | 13.49 | 12.84 | 1 | 1.74 | 2.27 | 20.1 | 19.2 | 0.9 | 22.1 | 19.7 | 2.4 | 22.2 | 20.5 | 1.7 | 421.5 | 772 | 350.5 | 1598.04 | NORMAL
7 |  | 2026-05-13 | PISC | L3 | AHU - I | YORK | SBH 250 DW | BENIHANA | 4 | 1450 | 9.1 | 7.3 | 7.2 | 7.1 | 7.1 | 7.1 | 7 | 0.2 | 0.1 | 0.1 | 18.5 | 17.3 | 1.2 | 22.5 | 21.1 | 1.4 | 22.4 | 20.8 | 1.6 | 541.6 | 662.3 | 120.7 | 1370.961 | NORMAL
8 |  | 2026-05-06 | PISC | L3 | AHU - I | DAIKIN | DDB 200 HR | SUSHI - TEI | 5.5 | 1450 | 12.1 | 7.9 | 7.91 | 7.7 | 7.8 | 7.89 | 7.71 | 0.1 | 0.02 | -0.01 | 17.8 | 16.7 | 1.1 | 21.9 | 20.1 | 1.8 | 21.9 | 19.8 | 2.1 | 679.3 | 902.5 | 223.2 | 1868.175 | NORMAL
9 |  | 2026-05-04 | PISC | L3 | AHU L3-16 | YORK | YDM 50 X 80 | OPPO | 11 | 1455 | 21.5 | 20.36 | 19.5 | 18.7 | 20.31 | 19.3 | 18.5 | 0.05 | 0.2 | 0.2 | 18.3 | 17.2 | 1.1 | 22.1 | 19.9 | 2.2 | 22.1 | 20 | 2.1 | 235.3 | 372.3 | 137 | 770.661 | NORMAL
10 |  | 2026-05-05 | PISC | L3 | AHU L3-19 | YORK | YDM 40 X 60 | GALLERY GHJ | 5.5 | 1450 | 12.1 | 8.47 | 8.87 | 8.23 | 7.98 | 8.35 | 7.73 | 0.49 | 0.52 | 0.5 | 18.3 | 17.1 | 1.2 | 21.9 | 20.1 | 1.8 | 22 | 21 | 1 | 614.6 | 837.2 | 222.6 | 1733.004 | NORMAL
11 |  | 2026-05-04 | PIE | L3 | AHU P3-01 | YORK | YDM 30 X 50 | CORRIDOR OPTIK MELAWAI | 3 | 1440 | 7.1 | 4.13 | 4.51 | 4.9 | 4.13 | 4.47 | 4.18 | 0 | 0.04 | 0.72 | 18.1 | 16.7 | 1.4 | 21.2 | 19.1 | 2.1 | 20.9 | 18.7 | 2.2 | 445.2 | 582.1 | 136.9 | 1204.947 | NORMAL
12 |  | 2026-05-01 | PIE | L3 | AHU P3-02 | YORK | YDM 30 X 50 | MARKS & SPENCER | 3 | 1440 | 7,1 | 5.3 | 5.5 | 5.2 | 5.2 | 5.2 | 5.1 | 0.1 | 0.3 | 0.1 | 18.5 | 16.7 | 1.8 | 21.8 | 19.8 | 2 | 21.5 | 19.6 | 1.9 | 543 | 701.8 | 158.8 | 1452.726 | NORMAL
13 |  | 2026-05-01 | PIE | L3 | AHU P3-02A | YORK | YDM 50 X 80 | MARKS & SPENCER | 11 | 1455 | 12,5 | 11.8 | 11.6 | 11.5 | 11.6 | 11.5 | 11.4 | 0.2 | 0.1 | 0.1 | 18.6 | 16.8 | 1.8 | 21.6 | 19.8 | 1.8 | 21.5 | 19.6 | 1.9 | 773 | 889.4 | 116.4 | 1841.058 | NORMAL
14 |  | 2026-05-01 | PIE | L3 | AHU P3-03 | YORK | YDM 60 X 80 | CORRIDOR SMIGGLE | 7.5 | 1450 | 16.2 | 6.76 | 7.7 | 6.97 | 6.61 | 7.33 | 6.8 | 0.15 | 0.37 | 0.17 | 18.4 | 17.1 | 1.3 | 21.4 | 20.1 | 1.3 | 21.2 | 20 | 1.2 | 407.7 | 715.1 | 307.4 | 1480.257 | NORMAL
15 |  | 2026-05-02 | PIE | L3 | AHU P3-07 | YORK | YDM 60 X 70 | MINIAPOLIS | 15 | 1455 | 27.7 | 24.54 | 26.6 | 24.8 | 24.46 | 26.2 | 24.7 | 0.08 | 0.4 | 0.1 | 18.7 | 17.3 | 1.4 | 22.1 | 20 | 2.1 | 22.1 | 19.7 | 2.4 | 428.2 | 573.2 | 145 | 1186.524 | NORMAL
16 |  | 2026-05-01 | PIE | L3 | AHU P3-08 | YORK | YDM 60 X 70 | ex. ROCK STAR GYM | 15 | 1450 | 29 | 26.33 | 27.98 | 26.52 | 14.12 | 15.74 | 14.67 | 12.21 | 12.24 | 11.85 | 18.1 | 16.8 | 1.3 | 22 | 20.7 | 1.3 | 21.9 | 20.5 | 1.4 | 411.7 | 715.1 | 303.4 | 1480.257 | NORMAL
17 |  | 2026-05-02 | PIE | L3 | AHU P3-09 | YORK | YDM 70 X 80 | MOTHER CARE | 15 | 1450 | 29 | 7.4 | 7.5 | 7.9 | 7.3 | 7.4 | 7.7 | 0.1 | 0.1 | 0.2 | 18.2 | 16.9 | 1.3 | 21.9 | 20.3 | 1.6 | 21.8 | 20.1 | 1.7 | 567 | 882 | 315 | 1825.74 | NORMAL
18 |  | 2026-05-08 | PISC | L4 | AHU L4-01 | YORK | YDM 50 X 120 | SERIBU RASA | 18.5 | 1450 | 34.4 | 10.2 | 10.5 | 10.1 | 9.9 | 10.1 | 9.98 | 0.3 | 0.4 | 0.12 | 18.9 | 17.8 | 1.1 | 22.8 | 21.6 | 1.2 | 22.5 | 21.4 | 1.1 | 761.3 | 842.1 | 80.8 | 1743.147 | NORMAL
19 |  | 2026-05-08 | PISC | L4 | AHU L4-02B | YORK | YDM 50 X 70 | TASTE PARADISE 001 | 7.5 | 1455 | 14.6 | 8.1 | 8.2 | 8 | 7.9 | 7.8 | 7.9 | 0.2 | 0.4 | 0.1 | 18.6 | 17.2 | 1.4 | 22.4 | 20.9 | 1.5 | 22.3 | 21.1 | 1.2 | 679.7 | 801.7 | 122 | 1659.519 | NORMAL
20 |  | 2026-05-08 | PISC | L4 | AHU L4-16 | YORK | YDM 50 X 70 | TASTE PARADISE 002 | 7.5 | 1455 | 14.6 | 8.17 | 8.58 | 7.66 | 8.07 | 8.51 | 6.01 | 0.1 | 0.07 | 1.65 | 18.6 | 17.2 | 1.4 | 22.4 | 20.9 | 1.5 | 22.4 | 21.2 | 1.2 | 592.4 | 799.1 | 206.7 | 1654.137 | NORMAL
21 |  | 2026-05-11 | PISC | L4 | AHU L4-12 | DAIKIN | DDM 1619 | LAMODA 01 | 7.5 | 1450 | 16.2 | 29.4 | 29.5 | 28.4 | 29.4 | 29.3 | 28.4 | 0 | 0.2 | 0 | 19.8 | 17.6 | 2.2 | 21.9 | 20.4 | 1.5 | 22 | 20.3 | 1.7 | 1077 | 1923 | 846 | 3980.61 | NORMAL
22 |  | 2026-05-11 | PISC | L4 | AHU L4-13 | DAIKIN | DDM 1619 | LAMODA 02 | 7.5 | 1450 | 16.2 | 29.1 | 25.6 | 14.3 | 29 | 25.5 | 14.3 | 0.1 | 0.1 | 0 | 19.9 | 17.8 | 2.1 | 21.8 | 20.2 | 1.6 | 22.1 | 20.1 | 2 | 1201 | 2304 | 1103 | 4769.28 | NORMAL
23 |  | 2026-05-10 | PISC | L4 | AHU - I | YORK | YDM SBH 250 DW | WATSON (AHU Gantung) | 4 | 1445 | 9.1 | 6.8 | 7 | 6.9 | 6.5 | 6.7 | 6.7 | 0.3 | 0.3 | 0.2 | 18.9 | 17.6 | 1.3 | 22.7 | 21.1 | 1.6 | 22.1 | 20.9 | 1.2 | 675 | 882 | 207 | 1825.74 | NORMAL
24 |  | 2026-05-13 | PISC | L4 | AHU L4-15 | YORK | YDM 50 X 80 | EIGHT TREASURE | 15 | 1450 | 29 | 23.5 | 23.6 | 23.5 | 23.4 | 23.4 | 23.4 | 0.1 | 0.2 | 0.1 | 19.1 | 16.9 | 2.2 | 22.9 | 20.7 | 2.2 | 22.5 | 20.5 | 2 | 588 | 678 | 90 | 1403.46 | NORMAL
25 |  | 2026-05-14 | PISC | L4 | AHU L4-17 | TRANE | CLCP 40 | RUANG TRAVO | 7.5 | 1455 | 14.6 | 6.73 | 7.14 | 6.65 | 6.76 | 7.04 | 6.57 | -0.03 | 0.1 | 0.08 | 17.9 | 16.6 | 1.3 | 22.4 | 20.9 | 1.5 | 22.1 | 20.6 | 1.5 | 197 | 435.3 | 238.3 | 901.071 | NORMAL
26 |  | 2026-05-07 | PISC | L4 | AHU L4 - I | YORK | YDM 50 X 120 | BUTTON SCARVES | 18.5 | 1450 | 34.4 | 11.3 | 11.9 | 12.5 | 10.6 | 11 | 12.2 | 0.7 | 0.9 | 0.3 | 18.5 | 17.1 | 1.4 | 23.4 | 21.3 | 2.1 | 23 | 20.9 | 2.1 | 458 | 678 | 220 | 1403.46 | NORMAL
27 |  | 2026-05-07 | PISC | L4 | AHU L4-II | TRANE | CLCP AE 68 | RIAMIRANDA | 11 | 1455 | 21.5 | 12.5 | 13 | 14.5 | 12 | 12.7 | 13.5 | 0.5 | 0.3 | 1 | 17.9 | 16.6 | 1.3 | 23.3 | 21.6 | 1.7 | 23 | 20.8 | 2.2 | 459 | 876 | 417 | 1813.32 | NORMAL
28 |  | 2026-05-07 | PISC | L4 | AHU L4-III | TRANE | CLCP AE 68 | BENANG JARUM | 11 | 1455 | 21.5 | 11.8 | 11.9 | 11 | 10.7 | 10 | 10.5 | 1.1 | 1.9 | 0.5 | 17.4 | 16.9 | 0.5 | 22.8 | 21.5 | 1.3 | 22.5 | 20.9 | 1.6 | 541 | 763 | 222 | 1579.41 | NORMAL
29 |  | 2026-05-12 | PISC | L4 | PAU L4-01 | TRANE | CLCP 040 | FRESH AIR 01 | 5.5 | 1460 | 11.4 | 11.22 | 8.96 | 8.36 | 6.33 | 4.45 | 4.47 | 4.89 | 4.51 | 3.89 | 18.3 | 17.1 | 1.2 | 23.1 | 21.7 | 1.4 | 22.8 | 21 | 1.8 | 445.2 | 677.6 | 232.4 | 1402.632 | NORMAL
30 |  | 2026-05-12 | PISC | L4 | PAU L4-02 | TRANE | CLCP 045 | FRESH AIR 02 | 7.5 | 1450 | 16.2 | 12.29 | 12.69 | 12.28 | 12.05 | 12.62 | 12.28 | 0.24 | 0.07 | 0 | 18.4 | 16.8 | 1.6 | 23.6 | 21.9 | 1.7 | 23.5 | 20.8 | 2.7 | 786 | 843.1 | 57.1 | 1745.217 | NORMAL
31 |  | 2026-05-12 | PISC | L4 | PAU L4-03 | TRANE | CLCP 045 | FRESH AIR 03 | 7.5 | 1450 | 16.2 | 11.01 | 11.42 | 10.96 | 10.79 | 11.02 | 10.73 | 0.22 | 0.4 | 0.23 | 19.1 | 17.3 | 1.8 | 23.4 | 21.8 | 1.6 | 23 | 20 | 3 | 573.2 | 630.4 | 57.2 | 1304.928 | NORMAL
32 |  | 2026-05-12 | PISC | L4 | PAU L4-04 | TRANE | CLCP 045 | FRESH AIR 04 | 7.5 | 1450 | 16.2 | 9.96 | 11 | 9.72 | 9.81 | 10.9 | 9.58 | 0.15 | 0.1 | 0.14 | 17.8 | 16.8 | 1 | 22.4 | 21 | 1.4 | 22.1 | 20.9 | 1.2 | 701.3 | 840.8 | 139.5 | 1740.456 | NORMAL
33 |  | 2026-05-14 | PISC | L4 | AHU L4-09 | TRANE | CLCP 045 | CORRIDOR LAVALEN | 11 | 1460 | 21.1 | 14 | 3.8 | 13.6 | 12.89 | 3.5 | 12.03 | 1.11 | 0.3 | 1.57 | 19.7 | 16.8 | 2.9 | 22.3 | 20.7 | 1.6 | 22.1 | 20.5 | 1.6 | 431.4 | 638.2 | 206.8 | 1321.074 | NORMAL
34 |  | 2026-05-31 | PIE | L4 | L4 | YORK | YDM SBH 125 | MORNINGSOL (AHU GANTUNG) | 4 | 1445 | 9.1 | 8.8 | 8.6 | 8.7 | 8.7 | 8.6 | 8.6 | 0.1 | 0 | 0.1 | 20.3 | 17.2 | 3.1 | 22.1 | 20.5 | 1.6 | 21.9 | 20.3 | 1.6 | 342 | 569 | 227 | 1177.83 | NORMAL
35 |  | 2026-05-16 | PIE | L4 | AHU P4-01 | YORK | YDM 30 X 50 | CORRIDOR ATRIUM / LOVE & FLAIR | 4 | 1445 | 9.1 | 4.88 | 5.44 | 5.22 | 4.77 | 5.23 | 5.09 | 0.11 | 0.21 | 0.13 | 20.4 | 17.3 | 3.1 | 21.9 | 20.4 | 1.5 | 21.6 | 20.2 | 1.4 | 451.7 | 665.8 | 214.1 | 1378.206 | NORMAL
36 |  | 2026-05-15 | PIE | L4 | AHU P4-02 | YORK | YDM 30 X 50 | CORRIDOR ATRIUM / LUCY HOUSE | 4 | 1445 | 9.1 | 5.22 | 5.12 | 5.1 | 5.2 | 4.99 | 5.01 | 0.02 | 0.13 | 0.09 | 20.3 | 16.9 | 3.4 | 22.2 | 21.1 | 1.1 | 22 | 20.9 | 1.1 | 320.7 | 557.1 | 236.4 | 1153.197 | NORMAL
37 |  | 2026-05-15 | PIE | L4 | AHU P4-03 | YORK | YDM 30 X 40 | CORRIDOR NOVERE | 3 | 1440 | 7.1 | 7.2 | 6.9 | 7.1 | 7.1 | 6.8 | 7.1 | 0.1 | 0.1 | 0 | 20.5 | 17 | 3.5 | 21.9 | 20.6 | 1.3 | 21.6 | 20.5 | 1.1 | 442 | 887 | 445 | 1836.09 | NORMAL
38 |  | 2026-05-16 | PIE | L4 | PAU P4-02 | YORK | YDM 40 X 70 | FRESH AIR FCU 001 | 7.5 | 1450 | 16.2 | 8.8 | 9.2 | 8.72 | 8.5 | 9 | 8.47 | 0.3 | 0.2 | 0.25 | 21 | 18.1 | 2.9 | 23.1 | 21 | 2.1 | 22.9 | 20.8 | 2.1 | 452 | 779 | 327 | 1612.53 | NORMAL
39 |  | 2026-05-16 | PIE | L4 | PAU P4-04 | YORK | YDM 40 X 70 | FRESH AIR FCU 002 | 7.5 | 1450 | 16.2 | 7.4 | 6.8 | 6.5 | 6.6 | 6.4 | 6.4 | 0.8 | 0.4 | 0.1 | 20.7 | 17.9 | 2.8 | 22.8 | 20.9 | 1.9 | 22.6 | 20.6 | 2 | 445 | 856 | 411 | 1771.92 | NORMAL
40 |  | 2026-05-15 | PIE | L4 | AHU P4-05 | YORK | YDM 40 X 60 | URBAN QUARTER / KOI THE | 15 | 1450 | 29 | 12 | 12.48 | 11.7 | 11.9 | 12.4 | 11.6 | 0.1 | 0.08 | 0.1 | 20.1 | 18.4 | 1.7 | 21.9 | 20.1 | 1.8 | 21.8 | 19.9 | 1.9 | 554 | 761 | 207 | 1575.27 | NORMAL
41 |  | 2026-05-15 | PIE | L4 | AHU P4-07 | YORK | YDM 60 X 80 | CORRIDOR TALENTA | 15 | 1450 | 29 | 16.4 | 13.3 | 12.56 | 12.2 | 12.9 | 12.48 | 4.2 | 0.4 | 0.08 | 19.9 | 17.9 | 2 | 20.9 | 19.8 | 1.1 | 21 | 19.7 | 1.3 | 549 | 688 | 139 | 1424.16 | NORMAL
42 |  | 2026-05-13 | PIE | L4 | AHU P4-09 | YORK | YDM 70 X 80 | CORRIDOR LIFT CP / KLAMBY | 15 | 1450 | 29 | 24.28 | 24.98 | 24.44 | 23.16 | 25 | 24.28 | 1.12 | -0.02 | 0.16 | 18.2 | 17.4 | 0.8 | 21.1 | 19.6 | 1.5 | 21.2 | 19.6 | 1.6 | 539.7 | 969.2 | 429.5 | 2006.244 | NORMAL
43 |  | 2026-05-18 | PIE | L5 | AHU P5-01 | YORK | YDM 50 X 60 | CORRIDOR CHOPSTIX | 4 | 1445 | 9.1 | 4.89 | 5.39 | 5.3 | 4.89 | 5.42 | 5.1 | 0 | -0.03 | 0.2 | 18.9 | 17.7 | 1.2 | 21.8 | 19.7 | 2.1 | 21.7 | 19.6 | 2.1 | 345.8 | 558.1 | 212.3 | 1155.267 | NORMAL
44 |  | 2026-05-18 | PIE | L5 | PAU P5-01 | YORK | YDM 30 X 50 | FRESH AIR FCU | 11 | 1455 | 20.9 | 17.2 | 17.4 | 17 | 17.1 | 17.2 | 16.9 | 0.1 | 0.2 | 0.1 | 18.7 | 16.8 | 1.9 | 22 | 19.8 | 2.2 | 21.9 | 19.7 | 2.2 | 439 | 761 | 322 | 1575.27 | NORMAL
45 | BMD-AHU-0056 | 2026-05-19 | PIE | L5 | AHU P5-02 | YORK | YDM 30 X 50 | CORRIDOR SATE SENAYAN | 4 | 1445 | 9.1 | 3.18 | 3.3 | 3.13 | 3.2 | 3.2 | 3.13 | -0.02 | 0.1 | 0 | 18.9 | 17.6 | 1.3 | 22.1 | 20.8 | 1.3 | 22.1 | 20.5 | 1.6 | 437.6 | 692.6 | 255 | 1433.682 | NORMAL
46 | BMD-AHU-0093 | 2026-05-27 | PIE | L5 | PAU P5-05 | YORK | YDM 30 X 50 | FRESH AIR FCU | 7.5 | 1450 | 16.2 | 12.4 | 12.3 | 12.1 | 12.3 | 12.1 | 12.1 | 0.1 | 0.2 | 0 | 19.3 | 17.8 | 1.5 | 22.8 | 20.9 | 1.9 | 22.7 | 21.1 | 1.6 | 410.2 | 644.3 | 234.1 | 1333.701 | NORMAL
47 | BMD-AHU-0098 | 2026-05-21 | PIE | L5 | AHU P5-05 | YORK | YDM 60 X 70 | GO WORK | 15 | 1445 | 27.5 | 27.51 | 28.2 | 27.17 | 27.34 | 28.1 | 26.75 | 0.17 | 0.1 | 0.42 | 19.2 | 17.9 | 1.3 | 22.6 | 21.3 | 1.3 | 22.5 | 20.9 | 1.6 | 712.2 | 943.3 | 231.1 | 1952.631 | NORMAL
48 |  | 2026-05-21 | PIE | L5 | AHU P5-06 | YORK | YDM 60 X 70 | ANGUS HOUSE | 15 | 1450 | 27.5 | 25.3 | 25.3 | 25 | 25.2 | 25.2 | 24.9 | 0.1 | 0.1 | 0.1 | 19.4 | 18.1 | 1.3 | 21.4 | 20.3 | 1.1 | 21.5 | 20.3 | 1.2 | 540 | 766 | 226 | 1585.62 | NORMAL
49 |  | 2026-05-18 | PIE | L5 | AHU P5-07 | YORK | YDM 40 X 60 | CORRIDOR LIFT CP / NIKA | 15 | 1450 | 27.5 | 21.4 | 21.7 | 21.2 | 21.3 | 21.3 | 21.2 | 0.1 | 0.4 | 0 | 19.3 | 18.3 | 1 | 23.4 | 22.1 | 1.3 | 23.4 | 22.2 | 1.2 | 544 | 871 | 327 | 1802.97 | NORMAL
50 |  | 2026-05-20 | PIE | L5 | AHU P5-09 | YORK | YDM 70 X 90 | RAMEN SEIROK-YA | 18.5 | 1450 | 34.4 | 12.2 | 11.86 | 13.69 | 11.43 | 11.44 | 12.66 | 0.77 | 0.42 | 1.03 | 19.2 | 18.1 | 1.1 | 22.8 | 21.5 | 1.3 | 22.5 | 21.5 | 1 | 864 | 942 | 78 | 1949.94 | NORMAL
51 |  | 2026-05-19 | PIE | L5 | AHU P5-10 | YORK | YDM 60 X 70 | CORRIDOR NIKA | 15 | 1450 | 29 | 24.7 | 24.3 | 24.3 | 24.6 | 24.3 | 24.2 | 0.1 | 0 | 0.1 | 19.4 | 17.8 | 1.6 | 22.6 | 21.2 | 1.4 | 22.7 | 21.2 | 1.5 | 349 | 559 | 210 | 1157.13 | NORMAL
52 |  | 2026-05-21 | PIE | L5 | AHU P5-11 | YORK | YDM 70 X 80 | WARE HOUSE | 15 | 1450 | 29 | 23.28 | 24.38 | 23.72 | 22.81 | 23.74 | 22.9 | 0.47 | 0.64 | 0.82 | 19.2 | 18.1 | 1.1 | 22.3 | 21 | 1.3 | 22.1 | 18.1 | 4 | 712.3 | 884.1 | 171.8 | 1830.087 | NORMAL
53 |  | 2026-05-26 | PISC | LB | AHU B1-01 | DAIKIN | DDW150DF | FOOD HALL 001 | 15 | 1470 | 29 | 17.26 | 16.3 | 18.5 | 16.7 | 15.9 | 17.1 | 0.56 | 0.4 | 1.4 | 18.2 | 16.6 | 1.6 | 22 | 20.5 | 1.5 | 21.8 | 20.4 | 1.4 | 445 | 663 | 218 | 1372.41 | NORMAL
54 |  | 2026-05-26 | PISC | LB | AHU B1-02 | DAIKIN | DDW150DF | FOOD HALL 002 | 15 | 1470 | 29 | 16.21 | 16.71 | 17.82 | 15.42 | 15.09 | 16.12 | 0.79 | 1.62 | 1.7 | 18.1 | 16.7 | 1.4 | 22.4 | 19.1 | 3.3 | 22.1 | 18.9 | 3.2 | 523 | 651 | 128 | 1347.57 | NORMAL
55 |  | 2026-05-22 | PISC | LB | AHU B1-03 | DAIKIN | DDM 1821 | FOOD HALL 003 | 7,5 | 1455 | 14,6 | 11.53 | 11.63 | 10.61 | 11.24 | 11.29 | 10.27 | 0.29 | 0.34 | 0.34 | 18.5 | 16.8 | 1.7 | 21.9 | 18.9 | 3 | 21.6 | 18.6 | 3 | 536 | 771 | 235 | 1595.97 | NORMAL
56 |  | 2026-05-22 | PISC | LB | AHU B1-04 | DAIKIN | DDM 1821 | FOOD HALL 004 | 7,5 | 1455 | 14,6 | 12.9 | 12 | 12 | 12.1 | 11.6 | 11.7 | 0.8 | 0.4 | 0.3 | 18.4 | 17.1 | 1.3 | 22.5 | 19.9 | 2.6 | 22.3 | 19.8 | 2.5 | 345 | 762 | 417 | 1577.34 | NORMAL
57 |  | 2026-05-23 | PISC | LB | AHU B1-05 | TRANE | CLCP 35 | FOOD HALL 005 | 7,5 | 1455 | 14,6 | 11.9 | 11.5 | 10.6 | 11.5 | 11.3 | 10 | 0.4 | 0.2 | 0.6 | 19 | 17.1 | 1.9 | 22.7 | 20.6 | 2.1 | 22.5 | 20.4 | 2.1 | 367 | 457 | 90 | 945.99 | NORMAL
58 |  | 2026-05-26 | PISC | LB | AHU B1-06 | DAIKIN | DDW150DB | CORRIDOR ACAII | 7.5 | 1455 | 14.6 | 9.04 | 8.64 | 8.49 | 8.93 | 8.6 | 8.44 | 0.11 | 0.04 | 0.05 | 18.9 | 16.8 | 2.1 | 21.8 | 20.1 | 1.7 | 21.7 | 20 | 1.7 | 675.1 | 882.9 | 207.8 | 1827.603 | NORMAL
59 |  | 2026-05-24 | PISC | LB | AHU B1-07 | TRANE | CLCP 20 | CORRIDOR GUARDIAN | 5,5 | 1460 | 11,4 | 8.9 | 9.01 | 8.88 | 8.65 | 8.82 | 8.78 | 0.25 | 0.19 | 0.1 | 18.2 | 17.1 | 1.1 | 22.5 | 20.5 | 2 | 22.3 | 20.4 | 1.9 | 512 | 660 | 148 | 1366.2 | NORMAL
60 |  | 2026-05-24 | PISC | LB | AHU B1-08 | TRANE | CLCP 40 | CORRIDOR TENGAH | 11 | 1460 | 21,1 | 18.1 | 18.3 | 17.9 | 17.9 | 18 | 17.8 | 0.2 | 0.3 | 0.1 | 18.4 | 17 | 1.4 | 22.5 | 20.3 | 2.2 | 22.1 | 20.1 | 2 | 452 | 679 | 227 | 1405.53 | NORMAL
61 |  | 2026-05-29 | PISC | LB | AHU B1-09 | TRANE | CLCP 20 | CORRIDOR PANORAMA | 3,7 | 1445 | 7,58 | 6.65 | 6.7 | 6.44 | 6.54 | 6.55 | 6.22 | 0.11 | 0.15 | 0.22 | 17.9 | 16.8 | 1.1 | 22.7 | 20.8 | 1.9 | 22.6 | 20.6 | 2 | 673 | 798 | 125 | 1651.86 | NORMAL
62 |  | 2026-05-17 | PISC | LB | AHU B1-10 | TRANE | CLCP 40 | CORRIDOR MAISON D'AURA | 11 | 1460 | 21,1 | 18.6 | 18.4 | 18.3 | 18.5 | 18.2 | 18.2 | 0.1 | 0.2 | 0.1 | 18.8 | 16.5 | 2.3 | 23.1 | 21.1 | 2 | 22.8 | 21 | 1.8 | 356 | 578 | 222 | 1196.46 | NORMAL
63 |  | 2026-05-24 | PISC | LB | AHU B1-11 | TRANE | CLCP 35 | CORRIDOR NEW FOODHALL | 18,5 | 1455 | 37,0 | 29.4 | 29.3 | 29.1 | 29.1 | 29.2 | 29.1 | 0.3 | 0.1 | 0 | 19 | 16.9 | 2.1 | 22.7 | 21.3 | 1.4 | 22.5 | 21 | 1.5 | 762 | 871 | 109 | 1802.97 | NORMAL
64 |  | 2026-05-23 | PISC | LB | AHU B1-12 | TRANE | CLCP 35 | CORRIDOR NEW FOODHALL | 15 | 1470 | 29 | 26.7 | 26.3 | 26.1 | 26.4 | 26.1 | 26.1 | 0.3 | 0.2 | 0 | 19.2 | 17.2 | 2 | 22.7 | 21.4 | 1.3 | 22.6 | 21.4 | 1.2 | 599 | 689 | 90 | 1426.23 | NORMAL
65 |  | 2026-05-23 | PISC | P2 | AHU - II | TRANE | ADZ 560 R | JHOP - 02 | 18,5 | 1455 | 37,0 | 9.03 | 9.04 | 8.4 | 8.73 | 8.33 | 8.3 | 0.3 | 0.71 | 0.1 | 17.3 | 16.2 | 1.1 | 22.8 | 21.2 | 1.6 | 22.5 | 21 | 1.5 | 569.3 | 774.6 | 205.3 | 1603.422 | NORMAL
66 |  | 2026-05-22 | PISC | P2 | AHU - 1 | DAIKIN | DDM 1821 | JHOP - 01 | 15 | 1470 | 29 | 9.76 | 9.7 | 8.6 | 9.46 | 9.5 | 8.1 | 0.3 | 0.2 | 0.5 | 17.1 | 16.2 | 0.9 | 22.8 | 21.2 | 1.6 | 22.5 | 21 | 1.5 | 601.2 | 769.2 | 168 | 1592.244 | NORMAL
Note on I15: ex. H & M
Note on I16: ex. H & M