## Actual-FCU
No | Date | Category | Floor | Area | Nama Tenant | Fcu Unit |  | Ampere (A) | [9 empty] | Diff. Temp (oC) |  |  | Room Temp (oC) |  |  | Jumlah Diffuser | Air Flow |  |  | Air Volume |  | Performance Unit | Reamaks
[8 empty] | Name Plate | Before |  |  | After |  |  | Margin | [9 empty] | ( Ft / M ) |  |  | ( CFM )
[6 empty] | Merk | Type |  | R | S | T | R | S | T | R | S | T | Before | After | Margin | Before | After | Margin |  | Before | After | Margin | Actual | Name Plate | ( % )
1 | 2026-05-01 | RETAIL | L2 | PIE | GUER LAIN 001 | DAIKIN | DDB 60 BW | 3,4 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 17.8 | 16.9 | 0.9 | 23.5 | 22.5 | 1 | 5 | 490 | 575 | 85 | 1983.75 | 2150 | 92.27% | NORMAL
2 | 2026-05-01 | RETAIL | L2 | PIE | GUER LAIN 002 | DAIKIN | DDB 60 BW | 3,4 | 2.4 |  |  | 2.3 |  |  | 0.1 | 0 | 0 | 17.5 | 16.8 | 0.7 | 23.6 | 22.6 | 1 | 5 | 405 | 595 | 190 | 2052.75 | 2150 | 95.48% | NORMAL
3 | 2026-05-01 | RETAIL | L2 | PIE | PAPILION DUO | MC QUAY | MCC 30 | 1,3 | 0.6 |  |  | 0.5 |  |  | 0.1 | 0 | 0 | 20.6 | 19.2 | 1.4 | 22.5 | 21.3 | 1.2 | 3 | 273 | 388 | 115 | 803.16 | 1000 | 80.32% | NORMAL | -
4 | 2026-05-09 | RETAIL | L2 | PIE | NARS 001 | MC QUAY | MCC 30 | 1,3 | 0.8 |  |  | 0.7 |  |  | 0.1 | 0 | 0 | 18.9 | 17.8 | 1.1 | 22 | 21.2 | 0.8 | 3 | 347 | 412 | 65 | 852.84 | 1000 | 85.28% | NORMAL | -
5 | 2026-05-09 | RETAIL | L2 | PIE | NARS 002 | MC QUAY | MCC 60 | 2,5 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 19.1 | 17.4 | 1.7 | 22 | 21.1 | 0.9 | 6 | 386 | 421 | 35 | 1742.94 | 2000 | 87.15% | NORMAL | -
6 | 2026-05-06 | RETAIL | L2 | PIE | LE LABO 001 | MC QUAY | MCC 60 | 2,5 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 19.4 | 18.1 | 1.3 | 22.1 | 20.6 | 1.5 | 4 | 472 | 627 | 155 | 1730.52 | 2000 | 86.53% | NORMAL
7 | 2026-05-06 | RETAIL | L2 | PIE | LE LABO 002 | MC QUAY | MCC 60 | 2,5 | 1.3 |  |  | 1.1 |  |  | 0.2 | 0 | 0 | 19.7 | 18.1 | 1.6 | 22.1 | 20.3 | 1.8 | 4 | 392 | 607 | 215 | 1675.32 | 2000 | 83.77% | NORMAL
8 | 2026-05-04 | F&B | L2 | PIE | PAUL BAKERY 001 | MC QUAY | MDB 75 | 3,4 | 2.5 |  |  | 2.4 |  |  | 0.1 | 0 | 0 | 19.7 | 18.4 | 1.3 | 23.5 | 22.3 | 1.2 | 5 | 416 | 585 | 169 | 2018.25 | 2500 | 80.73% | NORMAL | -
9 | 2026-05-04 | F&B | L2 | PIE | PAUL BAKERY 002 | MC QUAY | MDB 75 | 3,4 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 19.8 | 18.5 | 1.3 | 23.6 | 22.3 | 1.3 | 5 | 497 | 600 | 103 | 2070 | 2500 | 82.8% | NORMAL | -
10 | 2026-05-04 | F&B | L2 | PIE | PAUL BAKERY 003 | MC QUAY | MCC 60 | 2,5 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 19.3 | 18.5 | 0.8 | 23.1 | 22.3 | 0.8 | 5 | 316 | 464 | 148 | 1600.8 | 2000 | 80.04% | NORMAL | -
11 | 2026-05-04 | F&B | L2 | PIE | PAUL BAKERY 004 | MC QUAY | MDB 75 | 3,4 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 20.2 | 19.4 | 0.8 | 23.5 | 22.8 | 0.7 | 5 | 495 | 600 | 105 | 2070 | 2500 | 82.8% | NORMAL | -
12 | 2026-05-04 | RETAIL | L2 | PIE | DIPTYQUE PARIS | DAIKIN | DDB 115 BW | 2.89 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 16.4 | 15.8 | 0.6 | 22.3 | 22 | 0.3 | 6 | 730 | 861 | 131 | 3564.54 | 3850 | 92.59% | NORMAL | -
13 | 2026-05-01 | RETAIL | L2 | PIE | JO MALONE LONDON | DAIKIN | DDB 60 BW | 3.43 | 2.4 |  |  | 2.3 |  |  | 0.1 | 0 | 0 | 17.2 | 16.5 | 0.7 | 23.3 | 22 | 1.3 | 4 | 345 | 697 | 352 | 1923.72 | 2150 | 89.48% | NORMAL | -
14 | 2026-05-04 | RETAIL | L2 | PIE | SK-II | DAIKIN | DDB 75 BW | 3,4 | 2.6 |  |  | 2.4 |  |  | 0.2 | 0 | 0 | 18.5 | 17.6 | 0.9 | 22.5 | 21.7 | 0.8 | 4 | 525 | 760 | 235 | 2097.6 | 2500 | 83.9% | NORMAL | -
15 | 2026-05-07 | RETAIL | L2 | PIE | BYREDO | DAIKIN | DDB 60 BW | 3.43 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 18.7 | 16.6 | 2.1 | 21.1 | 20 | 1.1 | 4 | 578 | 700 | 122 | 1932 | 2150 | 89.86% | NORMAL | -
16 | 2026-05-03 | RETAIL | L2 | PIE | DYSON 001 | MC QUAY | MCC 60 | 2.5 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 19.6 | 18.3 | 1.3 | 22.4 | 21.6 | 0.8 | 6 | 348 | 430 | 82 | 1780.2 | 2000 | 89.01% | NORMAL | -
17 | 2026-05-03 | RETAIL | L2 | PIE | DYSON 002 | MC QUAY | MCC 60 | 2.5 | 1.5 |  |  | 1.3 |  |  | 0.2 | 0 | 0 | 18.5 | 17.6 | 0.9 | 22.9 | 22.6 | 0.3 | 6 | 235 | 400 | 165 | 1656 | 2000 | 82.8% | NORMAL | -
18 | 2026-05-02 | RETAIL | L2 | PIE | SAMSONITE | MC QUAY | MCC 60 | 2,5 | 1.4 |  |  | 1.2 |  |  | 0.2 | 0 | 0 | 18.2 | 17.5 | 0.7 | 22.9 | 22.5 | 0.4 | 4 | 454 | 589 | 135 | 1625.64 | 2000 | 81.28% | NORMAL | -
19 | 2026-05-02 | RETAIL | L2 | PIE | COLUMBIA | MC QUAY | MDB 75 | 3,4 | 2.4 |  |  | 2.2 |  |  | 0.2 | 0 | 0 | 19.6 | 18.7 | 0.9 | 22 | 21.3 | 0.7 | 7 | 335 | 430 | 95 | 2076.9 | 2500 | 83.08% | NORMAL | -
20 | 2026-05-02 | RETAIL | L2 | PIE | TUMI 001 | MC QUAY | MDB 75 | 3,4 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 18.7 | 17.6 | 1.1 | 22.9 | 21.7 | 1.2 | 8 | 290 | 375 | 85 | 2070 | 2500 | 82.8% | NORMAL | -
21 | 2026-05-02 | RETAIL | L2 | PIE | TUMI 002 | MC QUAY | MCC 30 | 1,3 | 0.5 |  |  | 0.4 |  |  | 0.1 | 0 | 0 | 19.8 | 18.1 | 1.7 | 23.9 | 22.7 | 1.2 | 3 | 287 | 392 | 105 | 811.44 | 1000 | 81.14% | NORMAL | -
22 | 2026-05-02 | RETAIL | L2 | PIE | RADO | MC QUAY | MCW 1200 | 0,7 | 0.3 |  |  | 0.2 |  |  | 0.1 | 0 | 0 | 17.6 | 16.9 | 0.7 | 22.9 | 22 | 0.9 | 4 | 230 | 355 | 125 | 979.8 | 1200 | 81.65% | NORMAL | -
23 | 2026-05-03 | RETAIL | L2 | PIE | HERSCHEL SUPPLY COMPANY | TRANE | HCCA 18 | 2,9 | 1.6 |  |  | 1.4 |  |  | 0.2 | 0 | 0 | 17.5 | 16.8 | 0.7 | 22.8 | 22.4 | 0.4 | 4 | 420 | 528 | 108 | 1457.28 | 1800 | 80.96% | NORMAL | -
24 | 2026-05-04 | RETAIL | L2 | PIE | PLANET SPORT 001 | TRANE | HCCA 24 | 4,9 | 3.4 |  |  | 3.3 |  |  | 0.1 | 0 | 0 | 19 | 18.6 | 0.4 | 20 | 19.7 | 0.3 | 8 | 375 | 396 | 21 | 2185.92 | 2400 | 91.08% | NORMAL
25 | 2026-05-04 | RETAIL | L2 | PIE | PLANET SPORT 002 | TRANE | HCCA 24 | 4,9 | 2.4 |  |  | 2.2 |  |  | 0.2 | 0 | 0 | 18.2 | 17.6 | 0.6 | 22.8 | 21.6 | 1.2 | 8 | 320 | 401 | 81 | 2213.52 | 2400 | 92.23% | NORMAL
26 | 2026-05-04 | RETAIL | L2 | PIE | PLANET SPORT 003 | TRANE | HCCA 24 | 4,9 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 18.3 | 17.8 | 0.5 | 22.3 | 21.6 | 0.7 | 8 | 318 | 405 | 87 | 2235.6 | 2400 | 93.15% | NORMAL
27 | 2026-05-04 | RETAIL | L2 | PIE | PLANET SPORT 004 | TRANE | HCCA 18 | 2,9 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 19.1 | 18.8 | 0.3 | 22.9 | 22.5 | 0.4 | 6 | 394 | 417 | 23 | 1726.38 | 1800 | 95.91% | NORMAL
28 | 2026-05-04 | RETAIL | L2 | PIE | CROCS | TRANE | HCCA 24 | 4,9 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 18.5 | 17.8 | 0.7 | 22.8 | 22.4 | 0.4 | 6 | 318 | 470 | 152 | 1945.8 | 2400 | 81.07% | NORMAL
29 | 2026-05-02 | RETAIL | L2 | PIE | SUSHI HIRO 001 | TRANE | HCCA 24 | 4.9 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 18.5 | 17.9 | 0.6 | 22.9 | 22.4 | 0.5 | 7 | 362 | 421 | 59 | 2033.43 | 2400 | 84.73% | NORMAL | -
30 | 2026-05-02 | RETAIL | L2 | PIE | SUSHI HIRO 002 | TRANE | HCCA 24 | 4.9 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 17.4 | 16.8 | 0.6 | 22.8 | 22.4 | 0.4 | 7 | 320 | 415 | 95 | 2004.45 | 2400 | 83.52% | NORMAL | -
31 | 2026-05-02 | RETAIL | L2 | PIE | SUSHI HIRO 003 | TRANE | HCCA 24 | 4.9 | 2.4 |  |  | 2.2 |  |  | 0.2 | 0 | 0 | 17.6 | 16 | 1.6 | 23 | 22.5 | 0.5 | 7 | 250 | 405 | 155 | 1956.15 | 2400 | 81.51% | NORMAL | -
32 | 2026-05-02 | RETAIL | L2 | PIE | SUSHI HIRO 004 | TRANE | HCCA 24 | 4.9 | 3.2 |  |  | 3.1 |  |  | 0.1 | 0 | 0 | 19.2 | 18.6 | 0.6 | 23.9 | 22.1 | 1.8 | 7 | 369 | 450 | 81 | 2173.5 | 2400 | 90.56% | NORMAL | -
33 | 2026-05-02 | RETAIL | L2 | PIE | BROWN PUCK COFFEE 001 | TRANE | HCCA 24 | 4.9 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 19.6 | 18.4 | 1.2 | 21.7 | 20.4 | 1.3 | 5 | 324 | 422 | 98 | 1455.9 | 1800 | 80.88% | NORMAL | -
34 | 2026-05-02 | RETAIL | L2 | PIE | BROWN PUCK COFFEE 002 | TRANE | HCCA 24 | 4.9 | 3.3 |  |  | 3.2 |  |  | 0.1 | 0 | 0 | 19.6 | 18.6 | 1 | 21.8 | 20.7 | 1.1 | 5 | 310 | 435 | 125 | 1500.75 | 1800 | 83.38% | NORMAL | -
35 | 2026-05-04 | F&B | L2 | PIE | BEBEK BENGIL 001 | MC QUAY | MDB 75 | 3,4 | 2.7 |  |  | 2.5 |  |  | 0.2 | 0 | 0 | 17.2 | 16.8 | 0.4 | 22.6 | 22.3 | 0.3 | 6 | 347 | 486 | 139 | 2012.04 | 2500 | 80.48% | NORMAL | -
36 | 2026-05-04 | F&B | L2 | PIE | BEBEK BENGIL 002 | YORK | SBH 100 DW | 8,8 | 5.3 |  |  | 5.2 |  |  | 0.1 | 0 | 0 | 17.5 | 17 | 0.5 | 22.9 | 22.2 | 0.7 | 6 | 530 | 695 | 165 | 2877.3 | 3200 | 89.92% | NORMAL | -
37 | 2026-05-04 | F&B | L2 | PIE | BEBEK BENGIL 003 | YORK | SBH 100 DW | 8,8 | 5.1 |  |  | 5 |  |  | 0.1 | 0 | 0 | 18.4 | 18.1 | 0.3 | 23.2 | 22.8 | 0.4 | 6 | 544 | 685 | 141 | 2835.9 | 3200 | 88.62% | NORMAL | -
38 | 2026-05-04 | F&B | L2 | PIE | BEBEK BENGIL 004 | MC QUAY | MCC 60 | 2,5 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 16.8 | 16.4 | 0.4 | 22.4 | 22.1 | 0.3 | 5 | 351 | 472 | 121 | 1628.4 | 2000 | 81.42% | NORMAL | -
39 | 2026-05-03 | F&B | L2 | PIE | NEW ERA | MC QUAY | MCC 30 | 1,3 | 0.5 |  |  | 0.4 |  |  | 0.1 | 0 | 0 | 18.1 | 17.6 | 0.5 | 22.4 | 21.8 | 0.6 | 6 | 105 | 200 | 95 | 828 | 1000 | 82.8% | NORMAL | -
40 | 2026-05-03 | F&B | L2 | PIE | CORRIDOR BEBEK BENGIL | MC QUAY | MCC 60 | 2,5 | 2.2 |  |  | 1.9 |  |  | 0.3 | 0 | 0 | 18.1 | 16.9 | 1.2 | 23.2 | 22 | 1.2 | 5 | 232 | 474 | 242 | 1635.3 | 2000 | 81.77% | NORMAL | -
41 | 2026-05-03 | BOH | L2 | PIE | CORRIDOR LIFT BARANG S1 & S2 | MC QUAY | MCC 30 | 1,3 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 20.7 | 19.3 | 1.4 | 24 | 23.5 | 0.5 | 2 | 470 | 600 | 130 | 828 | 1000 | 82.8% | NORMAL | -
42 | 2026-05-05 | BOH | L2 | PIE | TOILET CUSTOMER BEBEK BENGIL | TRANE | HCCA 14 | 1,8 | 1.2 |  |  | 1 |  |  | 0.2 | 0 | 0 | 21.1 | 20.1 | 1 | 24.3 | 23 | 1.3 | 5 | 200 | 350 | 150 | 1207.5 | 1400 | 86.25% | NORMAL | -
43 | 2026-05-04 | BOH | L2 | PIE | CORRIDOR JEMBATAN 001 | MC QUAY | MCC 60 | 2,5 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 16.2 | 15.8 | 0.4 | 21.2 | 21 | 0.2 | 4 | 368 | 582 | 214 | 1606.32 | 2000 | 80.32% | NORMAL | -
44 | 2026-05-04 | BOH | L2 | PIE | CORRIDOR JEMBATAN 002 | MC QUAY | MCC 60 | 2,5 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 17.8 | 17.3 | 0.5 | 23.5 | 23 | 0.5 | 4 | 430 | 590 | 160 | 1628.4 | 2000 | 81.42% | NORMAL | -
45 | 2026-05-02 | RETAIL | L2 | PIE | CONVERSE 001 | TRANE | HCCA 18 | 2,9 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 19.4 | 18.6 | 0.8 | 22.8 | 21.3 | 1.5 | 5 | 315 | 430 | 115 | 1483.5 | 1800 | 82.42% | NORMAL | -
46 | 2026-05-02 | RETAIL | L2 | PIE | CONVERSE 002 | TRANE | HCCA 18 | 2,9 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 19.6 | 18.4 | 1.2 | 21.8 | 20.9 | 0.9 | 5 | 315 | 425 | 110 | 1466.25 | 1800 | 81.46% | NORMAL | -
47 | 2026-05-03 | RETAIL | L2 | PIE | GOLF HOUSE 001 | TRANE | HCCA 24 | 4,9 | 2.3 |  |  | 2.1 |  |  | 0.2 | 0 | 0 | 18.9 | 17.8 | 1.1 | 23.6 | 22.6 | 1 | 5 | 450 | 565 | 115 | 1949.25 | 2400 | 81.22% | NORMAL | -
48 | 2026-05-03 | RETAIL | L2 | PIE | GOLF HOUSE 002 | TRANE | HCCA 10 | 1,3 | 0.8 |  |  | 0.7 |  |  | 0.1 | 0 | 0 | 19.5 | 18.6 | 0.9 | 23.7 | 22.7 | 1 | 3 | 236 | 393 | 157 | 813.51 | 1000 | 81.35% | NORMAL | -
49 | 2026-05-03 | RETAIL | L2 | PIE | GOLF HOUSE 003 | MCQUAY | MCC 40 | 1,9 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 19.5 | 18.6 | 0.9 | 23.5 | 22.1 | 1.4 | 5 | 250 | 362 | 112 | 1248.9 | 1500 | 83.26% | NORMAL | -
50 | 2026-05-02 | RETAIL | L2 | PIE | TEVA | TRANE | HCCA 14 | 1,8 | 1.4 |  |  | 1.2 |  |  | 0.2 | 0 | 0 | 17.6 | 16.9 | 0.7 | 22.5 | 21.9 | 0.6 | 6 | 220 | 355 | 135 | 1469.7 | 1800 | 81.65% | NORMAL | -
51 | 2026-05-02 | RETAIL | L2 | PIE | UNDER ARMOUR 001 | TRANE | HCCA 24 | 4,9 | 1.6 |  |  | 1.4 |  |  | 0.2 | 0 | 0 | 17.5 | 16.8 | 0.7 | 22.8 | 22.4 | 0.4 | 4 | 620 | 728 | 108 | 2009.28 | 2400 | 83.72% | NORMAL | -
52 | 2026-05-02 | RETAIL | L2 | PIE | UNDER ARMOUR 002 | TRANE | HCCA 24 | 4,9 | 3.2 |  |  | 3.1 |  |  | 0.1 | 0 | 0 | 19.5 | 18.6 | 0.9 | 23.4 | 22.7 | 0.7 | 4 | 521 | 715 | 194 | 1973.4 | 2400 | 82.22% | NORMAL | -
53 | 2026-05-02 | RETAIL | L2 | PIE | UNDER ARMOUR 003 | TRANE | HCCA 24 | 4,9 | 3.6 |  |  | 3.5 |  |  | 0.1 | 0 | 0 | 19.1 | 18.6 | 0.5 | 23.4 | 22.1 | 1.3 | 4 | 470 | 700 | 230 | 1932 | 2400 | 80.5% | NORMAL | -
54 | 2026-05-10 | RETAIL | L2 | PISC | PUMA | TRANE | HCCA 24 | 4,9 | 4 |  |  | 3.8 |  |  | 0.2 | 0 | 0 | 20.2 | 19.7 | 0.5 | 22.2 | 21.9 | 0.3 | 4 | 556 | 711 | 155 | 1962.36 | 2400 | 81.77% | NORMAL | -
55 | 2026-05-06 | RETAIL | L2 | PISC | NEW BALANCE 001 | TRANE | HCCA 24 | 4,9 | 2.4 |  |  | 2.2 |  |  | 0.2 | 0 | 0 | 18.7 | 17.9 | 0.8 | 22.1 | 21.7 | 0.4 | 4 | 615 | 730 | 115 | 2014.8 | 2400 | 83.95% | NORMAL | -
56 | 2026-05-06 | RETAIL | L2 | PISC | NEW BALANCE 002 | TRANE | HCCA 18 | 2.9 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 18.7 | 17.6 | 1.1 | 22.1 | 21.6 | 0.5 | 4 | 420 | 535 | 115 | 1476.6 | 1800 | 82.03% | NORMAL | -
57 | 2026-05-06 | RETAIL | L2 | PISC | ADIDAS 001 | TRANE | HCCA 18 | 2,9 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 17.1 | 16.2 | 0.9 | 22.1 | 21.7 | 0.4 | 4 | 420 | 535 | 115 | 1476.6 | 1800 | 82.03% | NORMAL | -
58 | 2026-05-06 | RETAIL | L2 | PISC | ADIDAS 002 | YORK | MAC 60 DW | 6,33 | 4.4 |  |  | 4.2 |  |  | 0.2 | 0 | 0 | 16.1 | 15.2 | 0.9 | 22.1 | 21.6 | 0.5 | 4 | 435 | 590 | 155 | 1628.4 | 1800 | 90.47% | NORMAL | -
59 | 2026-05-06 | RETAIL | L2 | PISC | ADIDAS 003 | YORK | MAC 60 DW | 6,33 | 4.1 |  |  | 4 |  |  | 0.1 | 0 | 0 | 19.1 | 18 | 1.1 | 21.4 | 20.2 | 1.2 | 5 | 493 | 667 | 174 | 2301.15 | 2500 | 92.05% | NORMAL | -
60 | 2026-05-06 | RETAIL | L2 | PISC | ADIDAS 004 | YORK | MAC 60 DW | 6,33 | 4.2 |  |  | 4.1 |  |  | 0.1 | 0 | 0 | 18.5 | 17.6 | 0.9 | 22.9 | 22 | 0.9 | 5 | 500 | 650 | 150 | 2242.5 | 2500 | 89.7% | NORMAL | -
61 | 2026-05-09 | RETAIL | L2 | PISC | AMARIS | MCQUAY | MCC 60 | 2,5 | 1.4 |  |  | 1.2 |  |  | 0.2 | 0 | 0 | 19 | 18.4 | 0.6 | 22.3 | 21.9 | 0.4 | 7 | 365 | 382 | 17 | 1845.06 | 2000 | 92.25% | NORMAL | -
62 | 2026-05-06 | BOH | L2 | PISC | CORRIDOR LIFT 1-2 | ITU | 1200 | 0,7 | 0.5 |  |  | 0.4 |  |  | 0.1 | 0 | 0 | 19.8 | 19.4 | 0.4 | 23.5 | 23 | 0.5 | 4 | 210 | 349 | 139 | 963.24 | 1200 | 80.27% | NORMAL
63 | 2026-05-07 | RETAIL | L2 | PISC | MAKE UP FOR EVER 001 | TRANE | HCCA 14 | 1,8 | 1.4 |  |  | 1.2 |  |  | 0.2 | 0 | 0 | 18.5 | 17.8 | 0.7 | 23.4 | 23 | 0.4 | 6 | 150 | 293 | 143 | 1213.02 | 1400 | 86.64% | NORMAL | -
64 | 2026-05-07 | RETAIL | L2 | PISC | MAKE UP FOR EVER 002 | MCQUAY | MDB 75 | 3,4 | 2.4 |  |  | 2.2 |  |  | 0.2 | 0 | 0 | 17.2 | 16.8 | 0.4 | 21.8 | 21.4 | 0.4 | 7 | 225 | 440 | 215 | 2125.2 | 2500 | 85.01% | NORMAL | -
65 | 2026-05-09 | RETAIL | L2 | PISC | LAURA MERCIER | MC QUAY | MCC 50 | 2,3 | 2 |  |  | 1.8 |  |  | 0.2 | 0 | 0 | 20.1 | 19.1 | 1 | 23 | 21.1 | 1.9 | 4 | 354 | 515 | 161 | 1421.4 | 1750 | 81.22% | NORMAL | -
66 | 2026-05-11 | RETAIL | L2 | PISC | LA MER | MC QUAY | MCC 50 | 2,3 | 1.8 |  |  | 1.7 |  |  | 0.1 | 0 | 0 | 17.1 | 13.9 | 3.2 | 23.7 | 22 | 1.7 | 4 | 336 | 510 | 174 | 1407.6 | 1750 | 80.43% | NORMAL | -
67 | 2026-05-10 | RETAIL | L2 | PISC | TOM FORD | YORK | SBH 50 DW | 4,21 | 2.22 |  |  | 2.1 |  |  | 0.12 | 0 | 0 | 19.8 | 18.7 | 1.1 | 23.3 | 22.5 | 0.8 | 5 | 292 | 434 | 142 | 1497.3 | 1600 | 93.58% | NORMAL | -
68 | 2026-05-05 | RETAIL | L2 | PISC | MASARI 001 | DAIKIN | DDB 50 BW | 3.7 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 18 | 17.5 | 0.5 | 22.4 | 21 | 1.4 | 4 | 326 | 552 | 226 | 1523.52 | 1700 | 89.62% | NORMAL
69 | 2026-05-05 | RETAIL | L2 | PISC | MASARI 002 | DAIKIN | DDB 50 BW | 3.7 | 3 |  |  | 2.9 |  |  | 0.1 | 0 | 0 | 18.6 | 18 | 0.6 | 22.8 | 21.5 | 1.3 | 4 | 317 | 566 | 249 | 1562.16 | 1700 | 91.89% | NORMAL
70 | 2026-05-05 | RETAIL | L2 | PISC | MASARI 003 | DAIKIN | DDB 60 BW | 3.43 | 2.6 |  |  | 2.4 |  |  | 0.2 | 0 | 0 | 18.2 | 17.5 | 0.7 | 22.3 | 21.7 | 0.6 | 4 | 530 | 705 | 175 | 1945.8 | 2150 | 90.5% | NORMAL
71 | 2026-05-04 | RETAIL | L2 | PISC | RODO | MCQUAY | MCC 50 | 2,3 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 18.9 | 16 | 2.9 | 23.4 | 22.7 | 0.7 | 4 | 490 | 525 | 35 | 1449 | 1750 | 82.8% | NORMAL | -
72 | 2026-05-09 | RETAIL | L2 | PISC | ONITSUKA TIGER 001 | MCQUAY | MCC 60 | 2,5 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 18.6 | 15.8 | 2.8 | 22.9 | 20.3 | 2.6 | 5 | 220 | 464 | 244 | 1600.8 | 2000 | 80.04% | NORMAL | -
73 | 2026-05-09 | RETAIL | L2 | PISC | ONITSUKA TIGER 002 | TRANE | HCCA 24 | 4,9 | 3.2 |  |  | 3.1 |  |  | 0.1 | 0 | 0 | 18.7 | 16.1 | 2.6 | 22.9 | 20 | 2.9 | 6 | 230 | 480 | 250 | 1987.2 | 2400 | 82.8% | NORMAL | -
74 | 2026-05-07 | RETAIL | L2 | PISC | ON JAKARTA 001 | MCQUAY | MCC 40 | 1.8 | 1.4 |  |  | 1.3 |  |  | 0.1 | 0 | 0 | 17.8 | 16.9 | 0.9 | 22.9 | 21.5 | 1.4 | 5 | 300 | 395 | 95 | 1362.75 | 1500 | 90.85% | NORMAL | -
75 | 2026-05-07 | RETAIL | L2 | PISC | ON JAKARTA 002 | MCQUAY | MCC 40 | 1.8 | 1.6 |  |  | 1.5 |  |  | 0.1 | 0 | 0 | 17.6 | 17 | 0.6 | 23 | 21.7 | 1.3 | 5 | 321 | 402 | 81 | 1386.9 | 1500 | 92.46% | NORMAL | -
76 | 2026-05-07 | RETAIL | L2 | PISC | ON JAKARTA 003 | MCQUAY | MCC 60 | 2,5 | 1.7 |  |  | 1.6 |  |  | 0.1 | 0 | 0 | 17.9 | 16.8 | 1.1 | 22.9 | 21.4 | 1.5 | 5 | 399 | 475 | 76 | 1638.75 | 2000 | 81.94% | NORMAL | -
77 | 2026-05-07 | RETAIL | L2 | PISC | ON JAKARTA 004 | TRANE | HCCA 10 | 1.3 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 20.1 | 18.5 | -1.6 | 22.2 | 21.7 | 0.5 | 4 | 275 | 316 | 41 | 872.16 | 1000 | 87.22% | NORMAL | -
78 | 2026-05-05 | RETAIL | L2 | PISC | ALO 001 | YORK | SBH 50 DW | 4.21 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 19.1 | 17.6 | 1.5 | 22.1 | 20.4 | 1.7 | 5 | 284 | 406 | 122 | 1400.7 | 1600 | 87.54% | NORMAL
79 | 2026-05-05 | RETAIL | L2 | PISC | ALO 002 | YORK | SBH 60 BW | 6,3 | 4.5 |  |  | 4.4 |  |  | 0.1 | 0 | 0 | 17.6 | 17.2 | 0.4 | 20.5 | 20.2 | 0.3 | 5 | 551 | 677 | 126 | 2335.65 | 2500 | 93.43% | NORMAL
80 | 2026-05-05 | RETAIL | L2 | PISC | ALO 003 | MCQUAY | MCC 60 | 2,5 | 1.5 |  |  | 1.3 |  |  | 0.2 | 0 | 0 | 16.6 | 15.7 | 0.9 | 20 | 20.4 | -0.4 | 5 | 318 | 465 | 147 | 1604.25 | 2000 | 80.21% | NORMAL
81 | 2026-05-05 | RETAIL | L2 | PISC | ALO 004 | MCQUAY | MCC 60 | 2,5 | 1.6 |  |  | 1.4 |  |  | 0.2 | 0 | 0 | 16.7 | 16.2 | 0.5 | 20.9 | 20.7 | 0.2 | 4 | 325 | 590 | 265 | 1628.4 | 2000 | 81.42% | NORMAL
82 | 2026-05-05 | RETAIL | L2 | PISC | ALO 005 | YORK | SBH 60 DW | 6,3 | 4.6 |  |  | 4.4 |  |  | 0.2 | 0 | 0 | 16.9 | 15.3 | 1.6 | 22.4 | 21.7 | 0.7 | 4 | 731 | 820 | 89 | 2263.2 | 2500 | 90.53% | NORMAL
83 | 2026-05-05 | RETAIL | L2 | PISC | ALO 006 | MCQUAY | MCC 60 | 2,5 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 19.6 | 18.7 | 0.9 | 22.7 | 21.8 | 0.9 | 5 | 433 | 497 | 64 | 1714.65 | 2000 | 85.73% | NORMAL
84 | 2026-05-05 | RETAIL | L2 | PISC | ALO 007 | YORK | SBH 60 DW | 6.3 | 4.8 |  |  | 4.7 |  |  | 0.1 | 0 | 0 | 19.5 | 19 | 0.5 | 23.1 | 22.7 | 0.4 | 5 | 357 | 385 | 28 | 1328.25 | 1500 | 88.55% | NORMAL
85 | 2026-05-05 | RETAIL | L2 | PISC | ALO 008 | MCQUAY | MCC 40 | 1,8 | 1.2 |  |  | 1.1 |  |  | 0.1 | 0 | 0 | 19.1 | 18.2 | 0.9 | 22.1 | 21 | 1.1 | 4 | 324 | 472 | 148 | 1302.72 | 1500 | 86.85% | NORMAL
86 | 2026-05-05 | RETAIL | L2 | PISC | ALO 009 | MCQUAY | MCC 40 | 1,8 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 19.7 | 18.4 | 1.3 | 22.7 | 21 | 1.7 | 4 | 337 | 467 | 130 | 1288.92 | 1500 | 85.93% | NORMAL
87 | 2026-05-06 | BOH | L2 | PISC | TOILET SW | TRANE | HCCA 14 | 1,9 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 19.9 | 19.5 | 0.4 | 23.7 | 23.2 | 0.5 | 4 | 240 | 425 | 185 | 1173 | 1400 | 83.79% | NORMAL
88 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 001 | TRANE | HCCA 14 | 1,8 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 17.7 | 16.3 | -1.4 | 22.9 | 22.1 | 0.8 | 4 | 302 | 412 | 110 | 1137.12 | 1400 | 81.22% | NORMAL | -
89 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 002 | YORK | YCC 60 C | 2,5 | 2.2 |  |  | 2.1 |  |  | 0.1 | 0 | 0 | 18.6 | 17.4 | 1.2 | 22.8 | 22 | 0.8 | 4 | 537 | 636 | 99 | 1755.36 | 2000 | 87.77% | NORMAL | -
90 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 003 | YORK | SBH 50 DW | 4,2 | 3.5 |  |  | 3.4 |  |  | 0.1 | 0 | 0 | 18.4 | 17.2 | 1.2 | 22.8 | 22 | 0.8 | 4 | 333 | 475 | 142 | 1311 | 1600 | 81.94% | NORMAL | -
91 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 004 | MC QUAY | MCC 40 | 1,9 | 1.5 |  |  | 1.4 |  |  | 0.1 | 0 | 0 | 18.8 | 18 | 0.8 | 22.8 | 22 | 0.8 | 4 | 318 | 455 | 137 | 1255.8 | 1500 | 83.72% | NORMAL | -
92 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 005 | TRANE | HCCA 14 | 1,8 | 1.5 |  |  | 1.2 |  |  | 0.3 | 0 | 0 | 17.4 | 16.6 | 0.8 | 22.8 | 22.4 | 0.4 | 4 | 315 | 415 | 100 | 1145.4 | 1400 | 81.81% | NORMAL | -
93 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 006 | TRANE | HCCA 10 | 1,3 | 0.5 |  |  | 0.4 |  |  | 0.1 | 0 | 0 | 17.1 | 16.2 | 0.9 | 23.6 | 22.3 | 1.3 | 4 | 188 | 295 | 107 | 814.2 | 1000 | 81.42% | NORMAL | -
94 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 007 | TRANE | HCCA 10 | 1,3 | 0.5 |  |  | 0.4 |  |  | 0.1 | 0 | 0 | 17.4 | 16.2 | 1.2 | 23.6 | 22.3 | 1.3 | 4 | 137 | 296 | 159 | 816.96 | 1000 | 81.7% | NORMAL | -
95 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 008 | YORK | YSB 60 BA | 2,3 | 2.9 |  |  | 2.7 |  |  | 0.2 | 0 | 0 | 18.5 | 17.6 | 0.9 | 23.1 | 22.1 | 1 | 4 | 293 | 662 | 369 | 1827.12 | 2000 | 91.36% | NORMAL | -
96 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 009 | TRANE | HCCA 14 | 1,8 | 1.4 |  |  | 1.2 |  |  | 0.2 | 0 | 0 | 17.5 | 16.8 | 0.7 | 22.9 | 22.4 | 0.5 | 6 | 170 | 278 | 108 | 1150.92 | 1400 | 82.21% | NORMAL | -
97 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 010 | DAIKIN | DDB 50 BW | 3,7 | 2.5 |  |  | 2.4 |  |  | 0.1 | 0 | 0 | 17.4 | 16.2 | -1.2 | 22.7 | 22.2 | 0.5 | 7 | 254 | 325 | 71 | 1569.75 | 1700 | 92.34% | NORMAL | -
98 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 011 | DAIKIN | DDB 50 BW | 3,7 | 3.6 |  |  | 3.5 |  |  | 0.1 | 0 | 0 | 18.5 | 17.1 | -1.4 | 22.6 | 21.8 | 0.8 | 4 | 451 | 562 | 111 | 1551.12 | 1700 | 91.24% | NORMAL | -
99 | 2026-05-11 | RETAIL | L2 | PISC | MASSIMO DUTI 012 | TRANE | HCCA 14 | 1,8 | 1.2 |  |  | 1.1 |  |  | 0.1 | 0 | 0 | 18 | 17.5 | -0.5 | 22.7 | 22.1 | 0.6 | 3 | 411 | 544 | 133 | 1126.08 | 1400 | 80.43% | NORMAL | -
100 | 2026-05-09 | RETAIL | L2 | PISC | OYSHO 001 | TRANE | HCCA 14 | 1,8 | 1.2 |  |  | 1.1 |  |  | 0.1 | 0 | 0 | 18.7 | 17.9 | 0.8 | 22.4 | 21.9 | 0.5 | 4 | 314 | 420 | 106 | 1159.2 | 1400 | 82.8% | NORMAL | -
101 | 2026-05-09 | RETAIL | L2 | PISC | OYSHO 002 | TRANE | HCCA 18 | 2,9 | 2.4 |  |  | 2.2 |  |  | 0.2 | 0 | 0 | 18.4 | 17.3 | 1.1 | 22.3 | 21.8 | 0.5 | 5 | 315 | 450 | 135 | 1552.5 | 1800 | 86.25% | NORMAL | -
102 | 2026-05-09 | RETAIL | L2 | PISC | OYSHO 003 | TRANE | HCCA 18 | 2,9 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 19.3 | 18.8 | 0.5 | 22.7 | 21.6 | 1.1 | 5 | 328 | 457 | 129 | 1576.65 | 1800 | 87.59% | NORMAL | -
103 | 2026-05-09 | RETAIL | L2 | PISC | OYSHO 004 | TRANE | HCCA 14 | 1.3 | 0.5 |  |  | 0.3 |  |  | 0.2 | 0 | 0 | 18.3 | 17.6 | 0.7 | 22.8 | 22.4 | 0.4 | 5 | 230 | 435 | 205 | 1500.75 | 1800 | 83.38% | NORMAL | -
104 | 2026-05-09 | RETAIL | L2 | PISC | OYSHO 005 | TRANE | HCCA 14 | 1,3 | 0.6 |  |  | 0.5 |  |  | 0.1 | 0 | 0 | 18.8 | 17.9 | 0.9 | 22.4 | 21.9 | 0.5 | 4 | 145 | 294 | 149 | 811.44 | 1000 | 81.14% | NORMAL | -
105 | 2026-05-09 | RETAIL | L2 | PISC | OYSHO 006 | TRANE | HCCA 10 | 1,3 | 1.2 |  |  | 1.1 |  |  | 0.1 | 0 | 0 | 18.1 | 17 | 1.1 | 22.1 | 21.8 | 0.3 | 4 | 241 | 300 | 59 | 828 | 1000 | 82.8% | NORMAL | -
106 | 2026-05-09 | RETAIL | L2 | PISC | OYSHO 007 | TRANE | HCCA 10 | 1,3 | 0.4 |  |  | 0.3 |  |  | 0.1 | 0 | 0 | 18.2 | 17.8 | 0.4 | 22.9 | 21.6 | 1.3 | 5 | 114 | 243 | 129 | 838.35 | 1000 | 83.83% | NORMAL | -
107 | 2026-05-07 | RETAIL | L2 | PISC | MAISON FRANCIS | YORK | MAC 75 DW | 6.33 | 5.7 |  |  | 5.6 |  |  | 0.1 | 0 | 0 | 19.9 | 18.9 | 1 | 23.2 | 21.7 | 1.5 | 4 | 630 | 765 | 135 | 2111.4 | 2500 | 84.46% | NORMAL | -
108 | 2026-05-09 | BOH | L2 | PISC | TOILET KARYAWAN | TRANE | HCCA 10 | 1,3 | 0.7 |  |  | 0.6 |  |  | 0.1 | 0 | 0 | 18.2 | 17.2 | 1 | 22.8 | 21.3 | 1.5 | 4 | 198 | 290 | 92 | 800.4 | 1000 | 80.04% | NORMAL | -
109 | 2026-05-20 | RETAIL | L2 | PISC | LACOSTE 001 | TRANE | HCCA 10 | 1,3 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 16.9 | 15.4 | 1.5 | 22.4 | 22.2 | 0.2 | 4 | 171 | 300 | 129 | 828 | 1000 | 82.8% | NORMAL | -
110 | 2026-05-20 | RETAIL | L2 | PISC | LACOSTE 002 | TRANE | HCCA 10 | 1,3 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 16.2 | 15.9 | 0.3 | 21.6 | 20.7 | 0.9 | 4 | 250 | 310 | 60 | 855.6 | 1000 | 85.56% | NORMAL | -
111 | 2026-05-20 | RETAIL | L2 | PISC | LACOSTE 003 | TRANE | HCCA 10 | 1,3 | 1.1 |  |  | 0.8 |  |  | 0.3 | 0 | 0 | 17.5 | 16.8 | 0.7 | 22.8 | 22.4 | 0.4 | 4 | 150 | 290 | 140 | 800.4 | 1000 | 80.04% | NORMAL | -
112 | 2026-05-07 | RETAIL | L2 | PISC | BALLY 001 | DAIKIN | DDB 50 BW | 3,7 | 2.6 |  |  | 2.4 |  |  | 0.2 | 0 | 0 | 19.3 | 18.6 | 0.7 | 21.8 | 21.2 | 0.6 | 5 | 325 | 574 | 249 | 1980.3 | 2150 | 92.11% | NORMAL | -
113 | 2026-05-07 | RETAIL | L2 | PISC | BALLY 002 | YORK | MAC 100 W15 | 8,8 | 5.4 |  |  | 5.3 |  |  | 0.1 | 0 | 0 | 17.7 | 16.6 | 1.1 | 23.2 | 22.1 | 1.1 | 6 | 513 | 699 | 186 | 2893.86 | 3200 | 90.43% | NORMAL | -
114 | 2026-05-07 | RETAIL | L2 | PISC | BALLY 003 | DAIKIN | DDB 50 BW | 3,7 | 2.4 |  |  | 2.3 |  |  | 0.1 | 0 | 0 | 18.6 | 17.4 | 1.2 | 21.7 | 19.9 | 1.8 | 5 | 497 | 578 | 81 | 1994.1 | 2150 | 92.75% | NORMAL | -
115 | 2026-05-07 | RETAIL | L2 | PISC | BALLY 004 | DAIKIN | DDB 50 BW | 3,7 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 17.3 | 16.6 | 0.7 | 22.5 | 21.7 | 0.8 | 5 | 318 | 565 | 247 | 1949.25 | 2150 | 90.66% | NORMAL | -
116 | 2026-05-07 | RETAIL | L2 | PISC | BALLY 005 | DAIKIN | DDB 40 BW | 3.40 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 19.4 | 18 | 1.4 | 21.7 | 20.1 | 1.6 | 5 | 277 | 346 | 69 | 1193.7 | 1250 | 95.5% | NORMAL | -
117 | 2026-05-09 | RETAIL | L2 | PISC | CREED | DAIKIN | DDB 40 BW | 3.6 | 2.4 |  |  | 2.2 |  |  | 0.2 | 0 | 0 | 18.3 | 17.8 | 0.5 | 23.2 | 22.9 | 0.3 | 4 | 330 | 435 | 105 | 1200.6 | 1250 | 96.05% | NORMAL | -
118 | 2026-05-01 | RETAIL | L2 | PISC | LOEWE | DAIKIN | DDB 50 BW | 4.21 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 17.6 | 16 | -1.6 | 23.1 | 22.7 | 0.4 | 5 | 315 | 423 | 108 | 1459.35 | 1600 | 91.21% | NORMAL | -
119 | 2026-05-07 | RETAIL | L2 | PISC | WEEKEND MAXMARA | DAIKIN | DDB 75 BW | 3.4 | 2.7 |  |  | 2.5 |  |  | 0.2 | 0 | 0 | 19.7 | 17.6 | 2.1 | 22.1 | 21.7 | 0.4 | 5 | 478 | 655 | 177 | 2259.75 | 2500 | 90.39% | NORMAL | -
120 | 2026-05-08 | RETAIL | L2 | PISC | CLE DE PEAU BEAUTE 001 | TRANE | HCCA 10 | 1,3 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 19.7 | 18.6 | 1.1 | 22.7 | 21.8 | 0.9 | 3 | 334 | 407 | 73 | 842.49 | 1000 | 84.25% | NORMAL | -
121 | 2026-05-08 | RETAIL | L2 | PISC | CLE DE PEAU BEAUTE 002 | TRANE | HCCA 10 | 1,3 | 1.06 |  |  | 1.02 |  |  | 0.04 | 0 | 0 | 18.6 | 16.9 | 1.7 | 22.1 | 21.2 | 0.9 | 4 | 155 | 305 | 150 | 841.8 | 1000 | 84.18% | NORMAL | -
122 | 2026-05-08 | RETAIL | L2 | PISC | CLE DE PEAU BEAUTE 003 | TRANE | HCCA 10 | 1,3 | 2.2 |  |  | 2.1 |  |  | 0.1 | 0 | 0 | 18.7 | 17.4 | 1.3 | 23.5 | 22.7 | 0.8 | 7 | 154 | 170 | 16 | 821.1 | 1000 | 82.11% | NORMAL | -
123 | 2026-05-07 | RETAIL | L2 | PISC | AIGNER 001 | TRANE | HCCA 18 | 2,9 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 17.7 | 16.9 | 0.8 | 21 | 20.1 | 0.9 | 3 | 621 | 740 | 119 | 1531.8 | 1800 | 85.1% | NORMAL | -
124 | 2026-05-07 | RETAIL | L2 | PISC | AIGNER 002 | MCQUAY | MCC 50 | 2.3 | 1.6 |  |  | 1.4 |  |  | 0.2 | 0 | 0 | 18.7 | 17.5 | 1.2 | 21.9 | 21 | 0.9 | 5 | 315 | 415 | 100 | 1431.75 | 1750 | 81.81% | NORMAL | -
125 | 2026-05-08 | RETAIL | L2 | PISC | COS 001 | DAIKIN | DDB 60 BW | 3.43 | 2.8 |  |  | 2.7 |  |  | 0.1 | 0 | 0 | 15.1 | 14.9 | 0.2 | 18.4 | 17.7 | 0.7 | 4 | 497 | 700 | 203 | 1932 | 2150 | 89.86% | NORMAL | -
126 | 2026-05-08 | RETAIL | L2 | PISC | COS 005 | DAIKIN | DDB 60 BW | 3.43 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 15.4 | 14.9 | 0.5 | 18.4 | 17.8 | 0.6 | 4 | 437 | 706 | 269 | 1948.56 | 2150 | 90.63% | NORMAL | -
127 | 2026-05-08 | RETAIL | L2 | PISC | COS 006 | DAIKIN | DDB 60 BW | 3.43 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 16.4 | 15.2 | 1.2 | 22.2 | 21 | 1.2 | 5 | 325 | 584 | 259 | 2014.8 | 2150 | 93.71% | NORMAL | -
128 | 2026-05-08 | RETAIL | L2 | PISC | COS 002 | DAIKIN | DDB 60 BW | 3.43 | 2.6 |  |  | 2.5 |  |  | 0.1 | 0 | 0 | 12.3 | 11.9 | 0.4 | 17.7 | 17.2 | 0.5 | 5 | 475 | 593 | -118 | 2045.85 | 2150 | 95.16% | NORMAL | -
129 | 2026-05-08 | RETAIL | L2 | PISC | COS 003 | DAIKIN | DDB 60 BW | 3.43 | 2.8 |  |  | 2.5 |  |  | 0.3 | 0 | 0 | 15.2 | 14.6 | 0.6 | 17.7 | 17.2 | 0.5 | 5 | 448 | 562 | 114 | 1938.9 | 2150 | 90.18% | NORMAL | -
130 | 2026-05-08 | RETAIL | L2 | PISC | COS 004 | DAIKIN | DDB 60 BW | 3.43 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 18.7 | 16.2 | 2.5 | 23 | 21.1 | 1.9 | 5 | 330 | 589 | 259 | 2032.05 | 2150 | 94.51% | NORMAL | -
131 | 2026-05-08 | RETAIL | L2 | PISC | COS 007 | DAIKIN | DDB 60 BW | 3.43 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 18.7 | 16.2 | 2.5 | 23.1 | 21 | 2.1 | 5 | 401 | 572 | 171 | 1973.4 | 2150 | 91.79% | NORMAL | -
132 | 2026-05-08 | RETAIL | L2 | PISC | COS 008 | DAIKIN | DDB 60 BW | 3.43 | 2 |  |  | 1.8 |  |  | 0.2 | 0 | 0 | 18.5 | 16.1 | 2.4 | 23.2 | 21 | 2.2 | 5 | 385 | 595 | 210 | 2052.75 | 2150 | 95.48% | NORMAL | -
133 | 2026-05-08 | RETAIL | L2 | PISC | COS 009 | DAIKIN | DDB 60 BW | 3.43 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 18.7 | 16 | 2.7 | 23.2 | 21.1 | 2.1 | 5 | 330 | 570 | 240 | 1966.5 | 2150 | 91.47% | NORMAL | -
134 | 2026-05-14 | RETAIL | L3 | PIE | OPTIK MELAWAI | MC QUAY | MCC 30 | 1,3 | 1 |  |  | 0.9 |  |  | 0.1 | 0 | 0 | 17.1 | 16.2 | -0.9 | 22.3 | 21.1 | 1.2 | 4 | 190 | 290 | 100 | 800.4 | 1000 | 80.04% | NORMAL | -
135 | 2026-05-12 | RETAIL | L3 | PIE | OPTIK SEIS 001 | MC QUAY | MCC 30 | 1,3 | 0.8 |  |  | 0.7 |  |  | 0.1 | 0 | 0 | 17.2 | 16.4 | 0.8 | 22.9 | 21.2 | 1.7 | 2 | 489 | 583 | 94 | 804.54 | 1000 | 80.45% | NORMAL | -
136 | 2026-05-12 | RETAIL | L3 | PIE | OPTIK SEIS 002 | MC QUAY | MDB 75 | 3,4 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 17.5 | 16.3 | 1.2 | 22.8 | 21.1 | 1.7 | 6 | 414 | 533 | 119 | 2206.62 | 2500 | 88.26% | NORMAL | -
137 | 2026-05-13 | RETAIL | L3 | PIE | PARANG KENCANA 001 | MC QUAY | MCC 30 | 1.3 | 0.7 |  |  | 0.6 |  |  | 0.1 | 0 | 0 | 19.2 | 18.8 | -0.4 | 22.8 | 22 | 0.8 | 4 | 244 | 316 | 72 | 872.16 | 1000 | 87.22% | NORMAL | -
138 | 2026-05-13 | RETAIL | L3 | PIE | PARANG KENCANA 002 | MC QUAY | MCC 60 | 2.5 | 2.2 |  |  | 2.1 |  |  | 0.1 | 0 | 0 | 17.7 | 17.5 | -0.2 | 22.9 | 22 | 0.9 | 7 | 232 | 345 | 113 | 1666.35 | 2000 | 83.32% | NORMAL | -
139 | 2026-05-12 | RETAIL | L3 | PIE | MUSIQUE 001 | ITU | 1200 | 0.7 | 0.5 |  |  | 0.4 |  |  | 0.1 | 0 | 0 | 19.4 | 18.5 | -0.9 | 24.5 | 23.8 | 0.7 | 7 | 155 | 214 | 59 | 1033.62 | 1200 | 86.13% | NORMAL | -
140 | 2026-05-12 | RETAIL | L3 | PIE | MUSIQUE 002 | MC QUAY | MDB 75 | 3.4 | 2.7 |  |  | 2.6 |  |  | 0.1 | 0 | 0 | 19.3 | 17.1 | -2.2 | 22.4 | 21.5 | 0.9 | 7 | 310 | 435 | 125 | 2101.05 | 2500 | 84.04% | NORMAL | -
141 | 2026-05-11 | RETAIL | L3 | PIE | STAR DIAMOND | MC QUAY | MCC 60 | 2.5 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 17.1 | 16.2 | 0.9 | 22.7 | 21 | 1.7 | 4 | 493 | 580 | 87 | 1600.8 | 2000 | 80.04% | NORMAL | -
142 | 2026-05-10 | F&B | L3 | PIE | THE RR CHOCOLATE 001 | MC QUAY | MDB 75 | 3,4 | 1.3 |  |  | 1.1 |  |  | 0.2 | 0 | 0 | 19.8 | 18.7 | 1.1 | 21.8 | 20.9 | 0.9 | 5 | 387 | 591 | 204 | 2038.95 | 2500 | 81.56% | NORMAL | -
143 | 2026-05-10 | F&B | L3 | PIE | THE RR CHOCOLATE 002 | YORK | SBH 125 | 3,7 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 19.1 | 17.7 | 1.4 | 22.7 | 20.8 | 1.9 | 7 | 578 | 755 | 177 | 3646.65 | 4100 | 88.94% | NORMAL | -
144 | 2026-05-11 | RETAIL | L3 | PIE | MARKS & SPENCER 001 | MC QUAY | MDB 75 | 3,4 | 2.7 |  |  | 2.6 |  |  | 0.1 | 0 | 0 | 19.8 | 18 | 1.8 | 20.3 | 19.5 | 0.8 | 7 | 275 | 442 | 167 | 2134.86 | 2500 | 85.39% | NORMAL | -
145 | 2026-05-11 | RETAIL | L3 | PIE | MARKS & SPENCER 002 | MC QUAY | MDB 75 | 3,4 | 2.9 |  |  | 2.7 |  |  | 0.2 | 0 | 0 | 19.9 | 17.7 | 2.2 | 23.4 | 22.6 | 0.8 | 5 | 418 | 570 | 152 | 1966.5 | 2500 | 78.66% | MEDIUM | -
146 | 2026-05-11 | RETAIL | L3 | PIE | MARKS & SPENCER 003 | MC QUAY | MDB 75 | 3,4 | 2.5 |  |  | 2.4 |  |  | 0.1 | 0 | 0 | 17.6 | 16.8 | 0.8 | 23 | 22.2 | 0.8 | 7 | 403 | 451 | 48 | 2178.33 | 2500 | 87.13% | NORMAL | -
147 | 2026-05-11 | RETAIL | L3 | PIE | MARKS & SPENCER 004 | MC QUAY | MDB 75 | 3,4 | 2.4 |  |  | 2.2 |  |  | 0.2 | 0 | 0 | 17.1 | 16.2 | -0.9 | 22.7 | 21 | 1.7 | 4 | 493 | 580 | 87 | 1600.8 | 2000 | 80.04% | NORMAL | -
148 | 2026-05-11 | RETAIL | L3 | PIE | MARKS & SPENCER 005 | MC QUAY | MCC 60 | 2,5 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 20.1 | 18.7 | 1.4 | 22.3 | 21.5 | 0.8 | 4 | 492 | 549 | 57 | 1515.24 | 2000 | 75.76% | MEDIUM | -
149 | 2026-05-11 | RETAIL | L3 | PIE | MARKS & SPENCER 006 | MC QUAY | MCC 60 | 2,5 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 18.6 | 17.5 | 1.1 | 22.7 | 21 | 1.7 | 6 | 315 | 410 | 95 | 1697.4 | 2000 | 84.87% | NORMAL | -
150 | 2026-05-11 | RETAIL | L3 | PIE | MARKS & SPENCER 007 | MC QUAY | MCC 60 | 2,5 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 16.5 | 15.2 | 1.3 | 22.7 | 21.3 | 1.4 | 5 | 452 | 510 | 58 | 1759.5 | 2000 | 87.98% | NORMAL | -
151 | 2026-05-12 | RETAIL | L3 | PIE | IBOX 001 | MC QUAY | MCC 60 | 2,5 | 1.7 |  |  | 1.6 |  |  | 0.1 | 0 | 0 | 18.4 | 17.9 | -0.5 | 23.3 | 22.2 | 1.1 | 4 | 455 | 594 | 139 | 1639.44 | 2000 | 81.97% | NORMAL | -
152 | 2026-05-12 | RETAIL | L3 | PIE | IBOX 002 | MC QUAY | MCC 60 | 2,5 | 1.4 |  |  | 1.3 |  |  | 0.1 | 0 | 0 | 18.4 | 17.9 | -0.5 | 23.3 | 22.2 | 1.1 | 4 | 416 | 584 | 168 | 1611.84 | 2000 | 80.59% | NORMAL | -
153 | 2026-05-12 | RETAIL | L3 | PIE | IBOX 003 | MC QUAY | MCC 60 | 2,5 | 1.8 |  |  | 1.7 |  |  | 0.1 | 0 | 0 | 17.6 | 16.6 | -1 | 22.8 | 22.1 | 0.7 | 4 | 430 | 580 | 150 | 1600.8 | 2000 | 80.04% | NORMAL | -
154 | 2026-05-12 | RETAIL | L3 | PIE | IBOX 004 | MC QUAY | MCC 60 | 2,5 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 18.2 | 17.1 | 1.1 | 23 | 22.1 | 0.9 | 4 | 414 | 585 | 171 | 1614.6 | 2000 | 80.73% | NORMAL | -
155 | 2026-05-10 | RETAIL | L3 | PIE | ELC | MC QUAY | MCC 60 | 2,5 | 1.2 |  |  | 1.1 |  |  | 0.1 | 0 | 0 | 19.7 | 17.6 | 2.1 | 20.9 | 19.7 | 1.2 | 6 | 327 | 398 | 71 | 1647.72 | 2000 | 82.39% | NORMAL | -
156 | 2026-05-14 | RETAIL | L3 | PIE | ZEIS VIXION CENTER 001 | MC QUAY | MDB 75 | 3,4 | 2 |  |  | 1.8 |  |  | 0.2 | 0 | 0 | 17.6 | 16.5 | 1.1 | 23.1 | 22.3 | 0.8 | 9 | 393 | 340 | 766 | 2111.4 | 2500 | 84.46% | NORMAL | -
157 | 2026-05-14 | RETAIL | L3 | PIE | ZEIS VIXION CENTER 002 | MC QUAY | MDB 75 | 3,4 | 2.2 |  |  | 2 |  |  | 0.2 | 0 | 0 | 17.8 | 16 | 1.8 | 22.3 | 21.4 | 0.9 | 7 | 399 | 431 | 32 | 2081.73 | 2500 | 83.27% | NORMAL | -
158 | 2026-05-10 | RETAIL | L3 | PIE | SUMERTIDE | MC QUAY | MCW 1200 | 0,7 | 0.3 |  |  | 0.2 |  |  | 0.1 | 0 | 0 | 19.7 | 18.1 | 1.6 | 21.2 | 19.9 | 1.3 | 4 | 234 | 353 | 119 | 974.28 | 1200 | 81.19% | NORMAL | -
159 | 2026-05-12 | RETAIL | L3 | PIE | CARTER'S AND SMIGGLE 001 | TRANE | HCCA 18 | 2,9 | 2.7 |  |  | 2.6 |  |  | 0.1 | 0 | 0 | 17.5 | 16.3 | 1.2 | 22.8 | 21.1 | 1.7 | 4 | 444 | 555 | 111 | 1531.8 | 1800 | 85.1% | NORMAL | -
160 | 2026-05-12 | RETAIL | L3 | PIE | CARTER'S AND SMIGGLE 002 | TRANE | HCCA 18 | 2,9 | 1.8 |  |  | 1.6 |  |  | 0.2 | 0 | 0 | 17.9 | 16.5 | 1.4 | 22.9 | 21.2 | 1.7 | 4 | 425 | 541 | 116 | 1493.16 | 1800 | 82.95% | NORMAL | -
161 | 2026-05-12 | RETAIL | L3 | PIE | ADIDAS KIDS 001 | TRANE | HCCA 18 | 2,9 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 16.8 | 15.8 | 1 | 22.6 | 21.3 | 1.3 | 4 | 435 | 523 | 88 | 1443.48 | 1800 | 80.19% | NORMAL | -
162 | 2026-05-12 | RETAIL | L3 | PIE | ADIDAS KIDS 002 | TRANE | HCCA 18 | 2,9 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 18.3 | 17.3 | 1 | 23.4 | 22.5 | 0.9 | 4 | 393 | 545 | 152 | 1504.2 | 1800 | 83.57% | NORMAL | -
163 | 2026-05-12 | RETAIL | L3 | PIE | ADIDAS KIDS 003 | TRANE | HCCA 18 | 2,9 | 1.4 |  |  | 1.3 |  |  | 0.1 | 0 | 0 | 18.3 | 17.1 | 1.2 | 23.5 | 22.4 | 1.1 | 4 | 401 | 529 | 128 | 1460.04 | 1800 | 81.11% | NORMAL | -
164 | 2026-05-22 | RETAIL | L3 | PIE | YAMAHA SMILE MUSIC 001 | AICOOL | FC 24 | 0.9 | 0.6 |  |  | 0.4 |  |  | 0.2 | 0 | 0 | 18.3 | 17.8 | 0.5 | 22.8 | 21.6 | 1.2 | 5 | 150 | 235 | 85 | 810.75 | 1000 | 81.07% | NORMAL
165 | 2026-05-22 | RETAIL | L3 | PIE | YAMAHA SMILE MUSIC 002 | AICOOL | FC 18 | 0.9 | 0.5 |  |  | 0.3 |  |  | 0.2 | 0 | 0 | 18.2 | 17.5 | 0.7 | 22.7 | 21.5 | 1.2 | 5 | 145 | 240 | 95 | 828 | 1000 | 82.8% | NORMAL
166 | 2026-05-22 | RETAIL | L3 | PIE | YAMAHA SMILE MUSIC 003 | TRANE | HCCA 14 | 1.8 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 17.8 | 16.4 | 1.4 | 22.7 | 22 | 0.7 | 5 | 230 | 345 | 115 | 1190.25 | 1400 | 85.02% | NORMAL
167 | 2026-05-22 | RETAIL | L3 | PIE | YAMAHA SMILE MUSIC 004 | TRANE | HCCA 24 | 4.9 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 15.5 | 14.7 | 0.8 | 22.3 | 21.5 | 0.8 | 7 | 321 | 410 | 89 | 1980.3 | 2400 | 82.51% | NORMAL
168 | 2026-05-22 | RETAIL | L3 | PIE | YAMAHA SMILE MUSIC 005 | TRANE | HCCA 24 | 4.9 | 4.5 |  |  | 4.4 |  |  | 0.1 | 0 | 0 | 16.8 | 15 | 1.8 | 21.5 | 20.3 | 1.2 | 7 | 236 | 402 | 166 | 1941.66 | 2400 | 80.9% | NORMAL
169 | 2026-05-22 | RETAIL | L3 | PIE | YAMAHA SMILE MUSIC 006 | TRANE | HCCA 24 | 4.9 | 4.2 |  |  | 4.1 |  |  | 0.1 | 0 | 0 | 19.4 | 18.7 | 0.7 | 22.7 | 22.2 | 0.5 | 7 | 332 | 441 | 109 | 2130.03 | 2400 | 88.75% | NORMAL
170 | 2026-05-22 | RETAIL | L3 | PIE | YAMAHA SMILE MUSIC 007 | TRANE | HCCA 24 | 4.9 | 2.8 |  |  | 2.7 |  |  | 0.1 | 0 | 0 | 18.6 | 17.7 | 0.9 | 22.8 | 22.1 | 0.7 | 7 | 358 | 451 | 93 | 2178.33 | 2400 | 90.76% | NORMAL
171 | 2026-05-22 | RETAIL | L3 | PIE | YAMAHA SMILE MUSIC 008 | TRANE | HCCA 24 | 4.9 | 2.4 |  |  | 2.2 |  |  | 0.2 | 0 | 0 | 17.6 | 16.2 | 1.4 | 22.8 | 22 | 0.8 | 7 | 354 | 405 | 51 | 1956.15 | 2400 | 81.51% | NORMAL
172 | 2026-05-22 | RETAIL | L3 | PIE | YAMAHA SMILE MUSIC 009 | TRANE | HCCA 10 | 1.3 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 19 | 18.2 | 0.8 | 22.8 | 21.5 | 1.3 | 4 | 137 | 315 | 178 | 869.4 | 1000 | 86.94% | NORMAL
173 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS SALON | TRANE | HCCA 18 | 2,9 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 17.9 | 17.2 | 0.7 | 23 | 22.3 | 0.7 | 4 | 413 | 522 | 109 | 1440.72 | 1800 | 80.04% | NORMAL | -
174 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS 001 | TRANE | HCCA 18 | 2,9 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 18.6 | 18 | 0.6 | 23 | 22.4 | 0.6 | 4 | 347 | 535 | 188 | 1476.6 | 1800 | 82.03% | NORMAL | -
175 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS 002 | TRANE | HCCA 24 | 4,9 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 18.9 | 18.1 | 0.8 | 22.8 | 22.2 | 0.6 | 4 | 635 | 760 | 125 | 2097.6 | 2400 | 87.4% | NORMAL | -
176 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS 003 | TRANE | HCCA 24 | 4,9 | 3.3 |  |  | 3.2 |  |  | 0.1 | 0 | 0 | 17.1 | 16.5 | 0.6 | 22.8 | 22.2 | 0.6 | 4 | 634 | 740 | 106 | 2042.4 | 2400 | 85.1% | NORMAL | -
177 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS 004 | TRANE | HCCA 24 | 4,9 | 3.5 |  |  | 3.4 |  |  | 0.1 | 0 | 0 | 18.5 | 17.9 | 0.6 | 22.6 | 22 | 0.6 | 6 | 355 | 470 | 115 | 1945.8 | 2400 | 81.07% | NORMAL | -
178 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS 005 | TRANE | HCCA 24 | 4,9 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 17.4 | 16.8 | 0.6 | 22.8 | 22.5 | 0.3 | 5 | 520 | 615 | 95 | 2121.75 | 2400 | 88.41% | NORMAL | -
179 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS 006 | TRANE | HCCA 24 | 4,9 | 2.4 |  |  | 2.2 |  |  | 0.2 | 0 | 0 | 17.5 | 16.8 | 0.7 | 22.9 | 22.5 | 0.4 | 5 | 418 | 565 | 147 | 1949.25 | 2400 | 81.22% | NORMAL | -
180 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS 007 | TRANE | HCCA 18 | 2,9 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 18.3 | 16.9 | 1.4 | 22.4 | 21.9 | 0.5 | 5 | 375 | 465 | 90 | 1604.25 | 1800 | 89.12% | NORMAL | -
181 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS 008 | TRANE | HCCA 18 | 2.9 | 1.8 |  |  | 1.7 |  |  | 0.1 | 0 | 0 | 18.2 | 17.3 | 0.9 | 23.1 | 22.7 | 0.4 | 7 | 164 | 315 | 151 | 1521.45 | 1800 | 84.53% | NORMAL | -
182 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS 009 | TRANE | HCCA 24 | 4,9 | 4.1 |  |  | 4 |  |  | 0.1 | 0 | 0 | 18.2 | 16 | 2.2 | 22.8 | 22 | 0.8 | 7 | 265 | 405 | 140 | 1956.15 | 2400 | 81.51% | NORMAL | -
183 | 2026-05-13 | RETAIL | L3 | PIE | MINIAPOLIS 010 | TRANE | HCCA 24 | 4,9 | 3.4 |  |  | 3.3 |  |  | 0.1 | 0 | 0 | 18.4 | 15.9 | 2.5 | 22.8 | 21.9 | 0.9 | 7 | 266 | 415 | 149 | 2004.45 | 2400 | 83.52% | NORMAL | -
184 | 2026-05-13 | BOH | L3 | PIE | TOILET BABY CHANGE | TRANE | HCCA 24 | 2.5 | 1.8 |  |  | 1.7 |  |  | 0.1 | 0 | 0 | 16.3 | 15.7 | 0.6 | 23.2 | 22.6 | 0.6 | 6 | 297 | 389 | 92 | 1610.46 | 2000 | 80.52% | NORMAL | -
185 | 2026-05-13 | BOH | L3 | PIE | CORRIDOR LIFT BARANG S1 & S2 | MC QUAY | MCC 30 | 1.3 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 17.2 | 16.5 | 0.7 | 23.1 | 22.7 | 0.4 | 4 | 230 | 300 | 70 | 828 | 1000 | 82.8% | NORMAL | -
186 | 2026-05-14 | RETAIL | L3 | PIE | KIDS STATION 001 | TRANE | HCCA 24 | 4.9 | 3.4 |  |  | 3.3 |  |  | 0.1 | 0 | 0 | 18.2 | 17.4 | 0.8 | 23.8 | 22.6 | 1.2 | 6 | 355 | 514 | 159 | 2127.96 | 2400 | 88.67% | NORMAL | -
187 | 2026-05-14 | RETAIL | L3 | PIE | KIDS STATION 002 | TRANE | HCCA 24 | 4.9 | 3.3 |  |  | 3.2 |  |  | 0.1 | 0 | 0 | 19.6 | 16.7 | 2.9 | 22.6 | 22.1 | 0.5 | 6 | 397 | 489 | 92 | 2024.46 | 2400 | 84.35% | NORMAL | -
188 | 2026-05-14 | RETAIL | L3 | PIE | ROCKSTAR GYM 003 | TRANE | HCCA 24 | 4.9 | 3.9 |  |  | 3.8 |  |  | 0.1 | 0 | 0 | 18.2 | 17.4 | 0.8 | 23.8 | 22.6 | 0.3 | 6 | 330 | 470 | 140 | 1945.8 | 2400 | 81.07% | NORMAL
189 | 2026-05-13 | RETAIL | L3 | PIE | OADKIDS 001 | TRANE | HCCA 18 | 2,9 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 18.2 | 17.4 | 0.8 | 23.4 | 22.6 | 0.8 | 4 | 459 | 556 | 97 | 1534.56 | 1800 | 85.25% | NORMAL | -
190 | 2026-05-13 | RETAIL | L3 | PIE | OADKIDS 002 | TRANE | HCCA 18 | 2,9 | 2.5 |  |  | 2.4 |  |  | 0.1 | 0 | 0 | 18.3 | 17.2 | 1.1 | 23.4 | 22.3 | 1.1 | 4 | 484 | 559 | 75 | 1542.84 | 1800 | 85.71% | NORMAL | -
191 | 2026-05-13 | RETAIL | L3 | PIE | OADKIDS 003 | TRANE | HCCA 18 | 2,9 | 2.4 |  |  | 2.3 |  |  | 0.1 | 0 | 0 | 15.2 | 13.6 | 1.6 | 23.3 | 21.1 | 2.2 | 4 | 489 | 539 | 50 | 1487.64 | 1800 | 82.65% | NORMAL | -
192 | 2026-05-13 | F&B | L3 | PIE | CAFÉ DE KALAHA | TRANE | HCCA 24 | 4.9 | 3.6 |  |  | 3.4 |  |  | 0.2 | 0 | 0 | 18.2 | 17.4 | 0.8 | 23.8 | 22.6 | 1.2 | 7 | 310 | 435 | 125 | 2101.05 | 2400 | 87.54% | NORMAL
193 | 2026-05-10 | RETAIL | L3 | PIE | STELLA MCCARTNEY KIDS | AICOOL | FC 24 | 0.9 | 0.2 |  |  | 0.1 |  |  | 0.1 | 0 | 0 | 18.6 | 17.7 | 0.9 | 23 | 21.2 | 1.8 | 4 | 230 | 300 | 70 | 828 | 1000 | 82.8% | NORMAL | -
194 | 2026-05-10 | RETAIL | L3 | PIE | BIMBI 001 | DAIKIN | DDB 50 BW | 3,7 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 18 | 16.5 | 1.5 | 23.1 | 20.1 | 3 | 4 | 300 | 594 | 294 | 1639.44 | 1700 | 96.44% | NORMAL | -
195 | 2026-05-10 | RETAIL | L3 | PIE | BIMBI 002 | DAIKIN | DDB 50 BW | 3,7 | 3.4 |  |  | 3.3 |  |  | 0.1 | 0 | 0 | 18.7 | 18.1 | 0.6 | 23.3 | 21.6 | 1.7 | 4 | 330 | 584 | 254 | 1611.84 | 1700 | 94.81% | NORMAL | -
196 | 2026-05-14 | RETAIL | L3 | PIE | PETIT BETEAU 001 | TRANE | HCCA 14 | 1.8 | 0.6 |  |  | 0.5 |  |  | 0.1 | 0 | 0 | 15.9 | 15.3 | 0.6 | 23.1 | 22.5 | 0.6 | 7 | 114 | 236 | 122 | 1139.88 | 1400 | 81.42% | NORMAL | -
197 | 2026-05-14 | RETAIL | L3 | PIE | PETIT BETEAU 002 | TRANE | HCCA 18 | 4.9 | 4 |  |  | 3.9 |  |  | 0.1 | 0 | 0 | 17.1 | 16.7 | 0.4 | 23 | 22.6 | 0.4 | 7 | 232 | 315 | 83 | 1521.45 | 1800 | 84.53% | NORMAL | -
198 | 2026-05-29 | RETAIL | P1 | PIE | MEISO | DAIKIN | DDB 50 BW | 3.7 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 19.3 | 18.8 | 0.5 | 23.1 | 22.6 | 0.5 | 4 | 410 | 557 | 147 | 1537.32 | 1700 | 90.43% | NORMAL
199 | 2026-05-16 | BOH | P1 | PIE | LOBBY LIFT CP 1,2 & 3 001 | YORK | SBH 100 DW | 8.8 | 7.8 |  |  | 7.7 |  |  | 0.1 | 0 | 0 | 19.7 | 18.2 | 1.5 | 23.6 | 22.9 | 0.7 | 4 | 875 | 989 | 114 | 2729.64 | 3200 | 85.3% | NORMAL | -
200 | 2026-05-16 | BOH | P1 | PIE | LOBBY LIFT CP 1,2 & 3 002 | TRANE | HCCA 24 | 4.9 | 3.7 |  |  | 3.6 |  |  | 0.1 | 0 | 0 | 19.5 | 18.7 | 0.8 | 23.6 | 22.9 | 0.7 | 4 | 596 | 725 | 129 | 2001 | 2400 | 83.37% | NORMAL | -
201 | 2026-05-16 | BOH | P2 | PIE | LOBBY LIFT CP 1,2 & 3 001 | YORK | SBH 100 DW | 8.8 | 5.7 |  |  | 5.6 |  |  | 0.1 | 0 | 0 | 18.2 | 17.5 | 0.7 | 23.1 | 22.7 | 0.4 | 4 | 821 | 976 | 155 | 2693.76 | 3200 | 84.18% | NORMAL | -
202 | 2026-05-16 | BOH | P2 | PIE | LOBBY LIFT CP 1,2 & 3 002 | TRANE | HCCA 24 | 4.9 | 4.2 |  |  | 4.1 |  |  | 0.1 | 0 | 0 | 18.5 | 17.8 | 0.7 | 23.2 | 22.6 | 0.6 | 4 | 600 | 715 | 115 | 1973.4 | 2400 | 82.22% | NORMAL | -
203 | 2026-05-16 | F&B | P2 | PIE | BAWAH TANGGA X PONUT | DAIKIN | DDB 100 BW | 7.4 | 6.7 |  |  | 6.5 |  |  | 0.2 | 0 | 0 | 17.2 | 16.4 | 0.8 | 23.3 | 22.6 | 0.7 | 5 | 613 | 785 | 172 | 2708.25 | 3200 | 84.63% | NORMAL | -
204 | 2026-05-18 | F&B | P2 | PIE | KANTINA 001 | MC QUAY | MCC 60 | 2.5 | 1.9 |  |  | 1.7 |  |  | 0.2 | 0 | 0 | 20.2 | 19.8 | -0.4 | 23.5 | 23 | 0.5 | 4 | 455 | 564 | 109 | 1556.64 | 2000 | 77.83% | MEDIUM | -
205 | 2026-05-18 | F&B | P2 | PIE | KANTINA 002 | TRANE | HCCA 18 | 2.9 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 19.7 | 18.7 | -1 | 23.5 | 22.5 | 1 | 4 | 314 | 470 | 156 | 1297.2 | 1800 | 72.07% | MEDIUM | -
206 | 2026-05-18 | F&B | P2 | PIE | KANTINA 003 | TRANE | HCCA 18 | 2.9 | 1.7 |  |  | 1.6 |  |  | 0.1 | 0 | 0 | 18.9 | 17.5 | -1.4 | 23.2 | 22.4 | 0.8 | 4 | 377 | 490 | 113 | 1352.4 | 1800 | 75.13% | MEDIUM | -
207 | 2026-05-18 | BOH | P3 | PIE | LOBBY LIFT CP 1,2 & 3 001 | TRANE | HCCA 18 | 2.9 | 1.4 |  |  | 1.3 |  |  | 0.1 | 0 | 0 | 18.8 | 18.2 | -0.6 | 23.4 | 23 | 0.4 | 4 | 450 | 540 | 90 | 1490.4 | 1800 | 82.8% | NORMAL | -
208 | 2026-05-18 | BOH | P3 | PIE | LOBBY LIFT CP 1,2 & 3 002 | TRANE | HCCA 18 | 2.9 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 20.2 | 17.5 | -2.7 | 23.4 | 22.6 | 0.8 | 4 | 435 | 535 | 100 | 1476.6 | 1800 | 82.03% | NORMAL | -
209 | 2026-05-25 | BOH | P4 | PIE | LOBBY LIFT CP 1,2 & 3 001 | DAIKIN | DDB 75 BW | 3.4 | 3.2 |  |  | 3.1 |  |  | 0.1 | 0 | 0 | 18.7 | 17.6 | 1.1 | 23.5 | 22.5 | 1 | 4 | 610 | 796 | 186 | 2196.96 | 2500 | 87.88% | NORMAL
210 | 2026-05-25 | BOH | P5 | PIE | LOBBY LIFT CP 1,2 & 3 002 | DAIKIN | DDB 75 BW | 3.4 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 18.6 | 17.3 | 1.3 | 23.2 | 22.4 | 0.8 | 4 | 625 | 746 | 121 | 2058.96 | 2500 | 82.36% | NORMAL
211 | 2026-05-24 | RETAIL | L3 | PISC | KENZO PARIS KIDS | TRANE | HCCA 18 | 2.9 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 18.6 | 18.2 | 0.4 | 22.4 | 21.2 | 1.2 | 6 | 220 | 380 | 160 | 1573.2 | 1800 | 87.4% | NORMAL
212 | 2026-05-23 | RETAIL | L3 | PISC | BOSS KIDS | TRANE | HCCA 18 | 2.9 | 2.5 |  |  | 2.4 |  |  | 0.1 | 0 | 0 | 19.7 | 17.2 | 2.5 | 22.8 | 22 | 0.8 | 6 | 289 | 389 | 100 | 1610.46 | 1800 | 89.47% | NORMAL
213 | 2026-05-14 | RETAIL | L3 | PISC | MIKI HOUSE 001 | TRANE | HCCA 10 | 1.3 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 19.7 | 16.5 | 3.2 | 22.5 | 22.3 | 0.2 | 4 | 435 | 522 | 87 | 1440.72 | 1800 | 80.04% | NORMAL | -
214 | 2026-05-14 | RETAIL | L3 | PISC | MIKI HOUSE 002 | TRANE | HCCA 18 | 2,9 | 2.4 |  |  | 2.3 |  |  | 0.1 | 0 | 0 | 18 | 18.1 | -0.1 | 23.1 | 22.3 | 0.8 | 4 | 415 | 525 | 110 | 1449 | 1800 | 80.5% | NORMAL | -
215 | 2026-05-14 | RETAIL | L3 | PISC | MIKI HOUSE 003 | TRANE | HCCA 18 | 2,9 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 18.1 | 17.3 | 0.8 | 23.2 | 22 | 1.2 | 4 | 420 | 535 | 115 | 1476.6 | 1800 | 82.03% | NORMAL
216 | 2026-05-14 | RETAIL | L3 | PISC | UNIQLO 001 | DAIKIN | DDB 115 BW | 2.89 | 2.2 |  |  | 2.1 |  |  | 0.1 | 0 | 0 | 18.7 | 17.6 | 1.1 | 22.5 | 21.6 | 0.9 | 6 | 683 | 845 | 162 | 3498.3 | 3850 | 90.86% | NORMAL | -
217 | 2026-05-14 | RETAIL | L3 | PISC | UNIQLO 002 | YORK | MAC 60 DW | 6.3 | 4.5 |  |  | 4.4 |  |  | 0.1 | 0 | 0 | 18.6 | 17.7 | 0.9 | 22.8 | 22.1 | 0.7 | 4 | 554 | 655 | 101 | 1807.8 | 2000 | 90.39% | NORMAL | -
218 | 2026-05-19 | RETAIL | L3 | PISC | MASSHIRO & CO 001 | MC QUAY | MCC 50 | 2.3 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 18.2 | 17.5 | 0.7 | 23.1 | 22.6 | 0.5 | 6 | 285 | 374 | 89 | 1548.36 | 1750 | 88.48% | NORMAL | -
219 | 2026-05-19 | RETAIL | L3 | PISC | MASSHIRO & CO 001 | MC QUAY | MCC 50 | 2.3 | 1.8 |  |  | 1.7 |  |  | 0.1 | 0 | 0 | 17.1 | 16.4 | 0.7 | 23 | 22.8 | 0.2 | 6 | 251 | 380 | 129 | 1573.2 | 1750 | 89.9% | NORMAL | -
220 | 2026-05-18 | RETAIL | L3 | PISC | WACOAL | MC QUAY | MCC 40 | 1,9 | 1.4 |  |  | 1.3 |  |  | 0.1 | 0 | 0 | 18.9 | 17.7 | 1.2 | 22.7 | 22 | 0.7 | 4 | 391 | 440 | -49 | 1214.4 | 1500 | 80.96% | NORMAL | -
221 | 2026-05-18 | RETAIL | L3 | PISC | SUKA CITA | TRANE | HCCA 18 | 2.9 | 1.5 |  |  | 1.4 |  |  | 0.1 | 0 | 0 | 19.7 | 17.2 | 2.5 | 22.8 | 22 | 0.8 | 6 | 198 | 375 | 177 | 1552.5 | 1800 | 86.25% | NORMAL
222 | 2026-05-24 | RETAIL | L3 | PISC | CZZARE | TRANE | HCCA 18 | 2.9 | 2 |  |  | 1.8 |  |  | 0.2 | 0 | 0 | 18 | 17.4 | 0.6 | 23.2 | 22.7 | 0.5 | 6 | 260 | 380 | 120 | 1573.2 | 1800 | 87.4% | NORMAL
223 | 2026-05-23 | RETAIL | L3 | PISC | A THAM TAILOR | TRANE | HCCA 18 | 2.9 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 20.3 | 17.8 | 2.5 | 23.7 | 22.9 | 0.8 | 6 | 211 | 382 | 171 | 1581.48 | 1800 | 87.86% | NORMAL
224 | 2026-05-10 | F&B | L3 | PISC | SOUP RESTAURANT 001 | YORK | SBH 100 | 8,8 | 5.8 |  |  | 4.9 |  |  | 0.9 | 0 | 0 | 20.3 | 19.4 | 0.9 | 23.7 | 22.5 | 1.2 | 6 | 501 | 672 | 171 | 2782.08 | 3200 | 86.94% | NORMAL | -
225 | 2026-05-10 | F&B | L3 | PISC | SOUP RESTAURANT 002 | MC QUAY | MCC 50 | 2,3 | 1.8 |  |  | 1.7 |  |  | 0.1 | 0 | 0 | 19.5 | 19 | 0.5 | 23 | 22.2 | 0.8 | 6 | 170 | 340 | 170 | 1407.6 | 1750 | 80.43% | NORMAL | -
226 | 2026-05-10 | F&B | L3 | PISC | SOUP RESTAURANT 003 | MC QUAY | MCC 60 | 2,5 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 20.1 | 19.5 | 0.6 | 22 | 21.8 | 0.2 | 6 | 304 | 426 | 122 | 1763.64 | 2000 | 88.18% | NORMAL | -
227 | 2026-05-10 | F&B | L3 | PISC | SOUP RESTAURANT 004 | MC QUAY | MCC 60 | 2,5 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 19.6 | 19.3 | 0.3 | 21.8 | 21.5 | 0.3 | 6 | 325 | 437 | 112 | 1809.18 | 2000 | 90.46% | NORMAL | -
228 | 2026-05-23 | RETAIL | L3 | PISC | TORENDA 001 | MC QUAY | MCC 60 | 2.5 | 2 |  |  | 1.8 |  |  | 0.2 | 0 | 0 | 18.6 | 18.2 | 0.4 | 23.3 | 22 | 1.3 | 6 | 310 | 387 | 77 | 1602.18 | 2000 | 80.11% | NORMAL
229 | 2026-05-23 | RETAIL | L3 | PISC | TORENDA 002 | DAIKIN | DDB 60 BW | 3,4 | 3.2 |  |  | 3.1 |  |  | 0.1 | 0 | 0 | 18.1 | 17.5 | 0.6 | 23.3 | 21.9 | 1.4 | 6 | 280 | 345 | 65 | 1428.3 | 1700 | 84.02% | NORMAL
230 | 2026-05-12 | RETAIL | L3 | PISC | THE DESIGNER WORKSHOP 001 | DAIKIN | DDB 60 BW | 3,4 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 17.8 | 16.9 | 0.9 | 23.5 | 22.5 | 1 | 4 | 490 | 654 | 164 | 1805.04 | 2150 | 83.96% | NORMAL | -
231 | 2026-05-12 | RETAIL | L3 | PISC | THE DESIGNER WORKSHOP 002 | MC QUAY | MCC 50 | 2.3 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 17.5 | 16.8 | 0.7 | 23.6 | 22.6 | 1 | 4 | 405 | 525 | 120 | 1449 | 1750 | 82.8% | NORMAL | -
232 | 2026-05-12 | RETAIL | L3 | PISC | THE DESIGNER WORKSHOP 003 | MC QUAY | MCC 50 | 2.3 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 19.9 | 17.8 | 2.1 | 23.6 | 22.3 | 1.3 | 4 | 336 | 544 | 208 | 1501.44 | 1750 | 85.8% | NORMAL | -
233 | 2026-05-12 | RETAIL | L3 | PISC | THE DESIGNER WORKSHOP 004 | TRANE | HCCA 14 | 2,9 | 1 |  |  | 0.9 |  |  | 0.1 | 0 | 0 | 17.9 | 16.8 | 1.1 | 23.6 | 22.1 | 1.5 | 4 | 300 | 424 | -124 | 1170.24 | 1400 | 83.59% | NORMAL | -
234 | 2026-05-16 | RETAIL | L3 | PISC | ex. PRIMA FIT 001 | MC QUAY | MCC 60 | 2,5 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 19.6 | 17.7 | 1.9 | 22.8 | 22.1 | 0.7 | 4 | 391 | 580 | 189 | 1600.8 | 2000 | 80.04% | NORMAL
235 | 2026-05-19 | F&B | L3 | PISC | JOE & DOUGH 001 | YORK | SBH 100 | 8,8 | 5.6 |  |  | 5.4 |  |  | 0.2 | 0 | 0 | 19.6 | 17.5 | 2.1 | 23.1 | 22.5 | 0.6 | 8 | 333 | 495 | 162 | 2732.4 | 3200 | 85.39% | NORMAL | -
236 | 2026-05-19 | F&B | L3 | PISC | JOE & DOUGH 002 | YORK | SBH 100 | 8,8 | 5.6 |  |  | 5.3 |  |  | 0.3 | 0 | 0 | 19.8 | 17.4 | 2.4 | 23.8 | 23.2 | 0.6 | 8 | 393 | 511 | 118 | 2820.72 | 3200 | 88.15% | NORMAL | -
237 | 2026-05-19 | F&B | L3 | PISC | JOE & DOUGH 003 | TRANE | HCCA 24 | 1,9 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 23.1 | 22.5 | 0.6 | 23.5 | 23.1 | 0.4 | 5 | 173 | 357 | -184 | 1231.65 | 1500 | 82.11% | NORMAL | -
238 | 2026-05-20 | BOH | L3 | PISC | CORRIDOR JOE & DOUGH 001 | MCQUAY | MCC 60 | 2.5 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 20.1 | 18.5 | 1.6 | 23.5 | 22.6 | 0.9 | 4 | 455 | 588 | 133 | 1622.88 | 2000 | 81.14% | NORMAL | -
239 | 2026-05-20 | BOH | L3 | PISC | CORRIDOR JOE & DOUGH 002 | MCQUAY | MCC 60 | 2.5 | 2.2 |  |  | 2 |  |  | 0.2 | 0 | 0 | 20.2 | 17.5 | 2.7 | 23.8 | 22.7 | 1.1 | 4 | 384 | 600 | 216 | 1656 | 2000 | 82.8% | NORMAL | -
240 | 2026-05-21 | RETAIL | L3 | PISC | REKHASTEXTILE 001 | TRANE | HCCA 18 | 2,9 | 2 |  |  | 1.8 |  |  | 0.2 | 0 | 0 | 18.2 | 17.3 | 0.9 | 23.4 | 22 | 1.4 | 6 | 315 | 352 | 37 | 1457.28 | 1800 | 80.96% | NORMAL | -
241 | 2026-05-21 | RETAIL | L3 | PISC | REKHASTEXTILE 002 | TRANE | HCCA 10 | 1,3 | 1.1 |  |  | 0.8 |  |  | 0.3 | 0 | 0 | 18.1 | 17.2 | 0.9 | 23.5 | 22.1 | 1.4 | 4 | 255 | 314 | 59 | 866.64 | 1000 | 86.66% | NORMAL | -
242 | 2026-05-21 | RETAIL | L3 | PISC | SEBASTIAN RED 001 | TRANE | HCCA 14 | 1,8 | 1.4 |  |  | 1.2 |  |  | 0.2 | 0 | 0 | 18.2 | 17.6 | 0.6 | 22.3 | 21.2 | 1.1 | 5 | 215 | 354 | 139 | 1221.3 | 1400 | 87.24% | NORMAL | -
243 | 2026-05-21 | RETAIL | L3 | PISC | SEBASTIAN RED 002 | TRANE | HCCA 18 | 2,9 | 1.2 |  |  | 1 |  |  | 0.2 | 0 | 0 | 17.8 | 17.2 | 0.6 | 22.3 | 21.1 | 1.2 | 6 | 208 | 348 | 140 | 1440.72 | 1800 | 80.04% | NORMAL | -
244 | 2026-05-15 | RETAIL | L3 | PISC | MOLTON BROWN | TRANE | HCCA 14 | 1,8 | 1.4 |  |  | 1.2 |  |  | 0.2 | 0 | 0 | 17.9 | 16.8 | 1.1 | 23.6 | 22.1 | 1.5 | 6 | 195 | 292 | 97 | 1208.88 | 1400 | 86.35% | NORMAL | -
245 | 2026-05-15 | RETAIL | L3 | PISC | THE GRAND PIANO | MC QUAY | MCC 60 | 2,5 | 1.6 |  |  | 1.5 |  |  | 0.1 | 0 | 0 | 18.2 | 17.5 | 0.7 | 22.7 | 22 | 0.7 | 4 | 389 | 590 | 201 | 1628.4 | 2000 | 81.42% | NORMAL | -
246 | 2026-05-15 | BOH | L3 | PISC | TOILET SW 001 | TRANE | HCCA 10 | 1.3 | 1 |  |  | 0.7 |  |  | 0.3 | 0 | 0 | 18.3 | 17.6 | 0.7 | 22.9 | 22.5 | 0.4 | 3 | 230 | 400 | 170 | 828 | 1000 | 82.8% | NORMAL | -
247 | 2026-05-15 | BOH | L3 | PISC | TOILET SW 002 | TRANE | HCCA 10 | 1.3 | 1.1 |  |  | 0.8 |  |  | 0.3 | 0 | 0 | 18.5 | 17.7 | 0.8 | 23.4 | 23 | 0.4 | 3 | 235 | 390 | 155 | 807.3 | 1000 | 80.73% | NORMAL | -
248 | 2026-05-15 | BOH | L3 | PISC | MUSHOLLA WANITA | DAIKIN | DDB 50 BW | 3,7 | 2.3 |  |  | 2.3 |  |  | 0 | 0 | 0 | 18.3 | 17.8 | 0.5 | 22.9 | 22.4 | 0.5 | 4 | 437 | 570 | 133 | 1573.2 | 1700 | 92.54% | NORMAL | -
249 | 2026-05-15 | BOH | L3 | PISC | MUSHOLLA PRIA | DAIKIN | DDB 75 BW | 3,4 | 2.2 |  |  | 2.2 |  |  | 0 | 0 | 0 | 18.6 | 17.4 | 1.2 | 22.9 | 22.5 | 0.4 | 4 | 635 | 800 | 165 | 2208 | 2500 | 88.32% | NORMAL | -
250 | 2026-05-19 | RETAIL | L3 | PISC | BANK MANDIRI 001 | MC QUAY | MCC 60 | 2.5 | 2.4 |  |  | 2 |  |  | 0.4 | 0 | 0 | 19.5 | 17.2 | 2.3 | 22.8 | 22.2 | 0.6 | 6 | 292 | 387 | 95 | 1602.18 | 2000 | 80.11% | NORMAL | -
251 | 2026-05-19 | RETAIL | L3 | PISC | BANK MANDIRI 002 | MC QUAY | MCC 60 | 2.5 | 2.2 |  |  | 2.1 |  |  | 0.1 | 0 | 0 | 19.5 | 17.2 | 2.3 | 22.7 | 22.1 | 0.6 | 6 | 291 | 395 | 104 | 1635.3 | 2000 | 81.76% | NORMAL | -
252 | 2026-05-19 | RETAIL | L3 | PISC | BANK MANDIRI 003 | MC QUAY | MCC 50 | 2.3 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 18.5 | 17.3 | 1.2 | 23.3 | 21.5 | 1.8 | 6 | 279 | 377 | 98 | 1560.78 | 1750 | 89.19% | NORMAL | -
253 | 2026-05-17 | RETAIL | L3 | PISC | HARLAN + HOLDEN 01 | MC QUAY | MCC 60 | 2,5 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 19.6 | 17.7 | 1.9 | 22.8 | 22.1 | 0.7 | 4 | 491 | 594 | 103 | 1639.44 | 2000 | 81.97% | NORMAL | -
254 | 2026-05-17 | RETAIL | L3 | PISC | HARLAN + HOLDEN 02 | MC QUAY | MCC 60 | 2.5 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 19 | 18.7 | 0.3 | 23.9 | 22.3 | 1.6 | 4 | 494 | 615 | 121 | 1697.4 | 2000 | 84.87% | NORMAL | -
255 | 2026-05-17 | RETAIL | L3 | PISC | HARLAN + HOLDEN 03 | MC QUAY | MCC 60 | 2.5 | 1.8 |  |  | 1.6 |  |  | 0.2 | 0 | 0 | 19.7 | 18 | 1.7 | 24.1 | 23 | 1.1 | 4 | 415 | 595 | 180 | 1642.2 | 2000 | 82.11% | NORMAL | -
256 | 2026-05-17 | RETAIL | L3 | PISC | HARLAN + HOLDEN 04 | TRANE | HCCA 18 | 2,9 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 19.5 | 18.4 | 1.1 | 22.4 | 21.2 | 1.2 | 4 | 520 | 610 | 90 | 1683.6 | 2000 | 84.18% | NORMAL | -
257 | 2026-05-16 | RETAIL | L3 | PISC | PILLAR 001 | DAIKIN | DDB 50 BW | 3,7 | 2.3 |  |  | 2.1 |  |  | 0.2 | 0 | 0 | 19.7 | 17.4 | 2.3 | 22.8 | 22 | 0.8 | 4 | 481 | 555 | 74 | 1531.8 | 1700 | 90.11% | NORMAL | -
258 | 2026-05-16 | RETAIL | L3 | PISC | PILLAR 002 | DAIKIN | DDB 50 BW | 3,7 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 19.4 | 17 | 2.4 | 22.8 | 21.7 | 1.1 | 4 | 453 | 564 | 111 | 1556.64 | 1700 | 91.57% | NORMAL | -
259 | 2026-05-16 | RETAIL | L3 | PISC | PILLAR 003 | DAIKIN | DDB 50 BW | 3,7 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 18 | 17.4 | 0.6 | 23.2 | 22.8 | 0.4 | 5 | 375 | 455 | 80 | 1569.75 | 1700 | 92.34% | NORMAL | -
260 | 2026-05-16 | RETAIL | L3 | PISC | PILLAR 004 | DAIKIN | DDB 50 BW | 3,7 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 18.1 | 17.6 | 0.5 | 23.1 | 22.4 | 0.7 | 5 | 348 | 460 | 112 | 1587 | 1700 | 93.35% | NORMAL | -
261 | 2026-05-19 | RETAIL | L3 | PISC | PASSION PRIVE 001 | TRANE | HCCA 18 | 1.8 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 19.6 | 17.6 | 2 | 22.7 | 22 | 0.7 | 5 | 256 | 420 | 164 | 1449 | 1800 | 80.5% | NORMAL | -
262 | 2026-05-19 | RETAIL | L3 | PISC | PASSION PRIVE 002 | DAIKIN | DDB 50 BW | 3,7 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 19.6 | 17.7 | 1.9 | 22.8 | 22.1 | 0.7 | 4 | 391 | 580 | 189 | 1600.8 | 1700 | 94.16% | NORMAL | -
263 | 2026-05-18 | RETAIL | L3 | PISC | YANTI JEWELL | TRANE | HCCA 14 | 1.8 | 1.3 |  |  | 1 |  |  | 0.3 | 0 | 0 | 18.6 | 18.2 | 0.4 | 22.3 | 21.8 | 0.5 | 4 | 356 | 421 | 65 | 1161.96 | 1400 | 83% | NORMAL | -
264 | 2026-05-26 | RETAIL | L3 | PISC | ALCHEMIST | TRANE | HCCA 14 | 1.8 | 1.1 |  |  | 0.9 |  |  | 0.2 | 0 | 0 | 18.1 | 17.5 | 0.6 | 22.9 | 22.3 | 0.6 | 4 | 377 | 411 | 34 | 1134.36 | 1400 | 81.03% | NORMAL
265 | 2026-05-18 | RETAIL | L3 | PISC | VERDE 001 | DAIKIN | DDB 60 BW | 3.43 | 2 |  |  | 1.8 |  |  | 0.2 | 0 | 0 | 19.2 | 17.8 | 1.4 | 22.8 | 21.8 | 1 | 4 | 558 | 700 | 142 | 1932 | 2150 | 89.86% | NORMAL | -
266 | 2026-05-18 | RETAIL | L3 | PISC | VERDE 002 | TRANE | HCCA 10 | 1.3 | 1.1 |  |  | 0.8 |  |  | 0.3 | 0 | 0 | 17.8 | 16.9 | 0.9 | 23.5 | 22.5 | 1 | 4 | 190 | 300 | 110 | 828 | 1000 | 82.8% | NORMAL | -
267 | 2026-05-18 | RETAIL | L3 | PISC | VERDE 003 | TRANE | HCCA 24 | 4.9 | 2.2 |  |  | 2.1 |  |  | 0.1 | 0 | 0 | 18.2 | 17.5 | 0.7 | 23.1 | 22.6 | 0.5 | 6 | 285 | 494 | 209 | 2045.16 | 2400 | 85.22% | NORMAL | -
268 | 2026-04-23 | RETAIL | L3 | PISC | FRANK & C0 001 | DAIKIN | DDB 60 BW | 3.43 | 2.2 |  |  | 2.2 |  |  | 0 | 0 | 0 | 18.2 | 17.3 | 0.9 | 22.5 | 21.1 | 1.4 | 6 | 208 | 498 | 290 | 2061.72 | 2150 | 95.89% | NORMAL
269 | 2026-04-23 | RETAIL | L3 | PISC | FRANK & CO 002 | DAIKIN | DDB 60 BW | 3.43 | 2 |  |  | 1.8 |  |  | 0.2 | 0 | 0 | 18.1 | 17.2 | 0.9 | 22.3 | 21.2 | 1.1 | 6 | 285 | 496 | 211 | 2053.44 | 2150 | 95.51% | NORMAL
270 | 2026-05-17 | RETAIL | L3 | PISC | ADELLE JEWELLERY 001 | DAIKIN | DDB 60 BW | 3.43 | 2.4 |  |  | 2.3 |  |  | 0.1 | 0 | 0 | 18.9 | 18.4 | 0.5 | 22.2 | 21.8 | 0.4 | 5 | 493 | 610 | 117 | 2104.5 | 2150 | 97.88% | NORMAL
271 | 2026-05-17 | RETAIL | L3 | PISC | ADELLE JEWELLERY 002 | DAIKIN | DDB 60 BW | 3.43 | 2.2 |  |  | 2.1 |  |  | 0.1 | 0 | 0 | 20.1 | 19.7 | 0.4 | 22.3 | 21.8 | 0.5 | 5 | 500 | 612 | 112 | 2111.4 | 2150 | 98.2% | NORMAL
272 | 2026-05-18 | BOH | L3 | PISC | TOILET KARYAWAN 002 | TRANE | HCCA 10 | 1.3 | 1 |  |  | 0.8 |  |  | 0.2 | 0 | 0 | 19.4 | 17.8 | 1.6 | 23.8 | 22.9 | 0.9 | 3 | 226 | 387 | 161 | 801.09 | 1000 | 80.11% | NORMAL | -
273 | 2026-05-18 | BOH | L3 | PISC | TOILET KARYAWAN 003 | TRANE | HCCA 10 | 1.3 | 0.9 |  |  | 0.7 |  |  | 0.2 | 0 | 0 | 19.8 | 18.7 | 1.1 | 23.2 | 22.8 | 0.4 | 3 | 218 | 390 | 172 | 807.3 | 1000 | 80.73% | NORMAL | -
274 | 2026-05-24 | F&B | L3 | PISC | BAM SENJU 001 | TRANE | HCCA 24 | 4.9 | 3.6 |  |  | 3.4 |  |  | 0.2 | 0 | 0 | 18.1 | 17.4 | 0.7 | 23 | 22 | 1 | 6 | 400 | 465 | 65 | 1925.1 | 2400 | 80.21% | NORMAL
275 | 2026-05-24 | F&B | L3 | PISC | BAM SENJU 002 | YORK | SBH 60 DW | 6.3 | 5.4 |  |  | 5.3 |  |  | 0.1 | 0 | 0 | 17.5 | 17 | 0.5 | 23.6 | 22.4 | 1.2 | 6 | 351 | 549 | 198 | 2272.86 | 2500 | 90.91% | NORMAL
276 | 2026-05-24 | F&B | L3 | PISC | BAM SENJU 003 | DAIKIN | DDB 60 BW | 3,4 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 18.9 | 17.8 | 1.1 | 23.4 | 22.9 | 0.5 | 6 | 399 | 445 | 46 | 1842.3 | 2150 | 85.69% | NORMAL
277 | 2026-05-24 | F&B | L3 | PISC | BAM SENJU 004 | TRANE | HCCA 24 | 4.9 | 3.7 |  |  | 3.5 |  |  | 0.2 | 0 | 0 | 18.6 | 17.2 | 1.4 | 23.5 | 22.6 | 0.9 | 6 | 415 | 495 | 80 | 2049.3 | 2400 | 85.39% | NORMAL
278 | 2026-05-27 | RETAIL | L3 | PISC | BENIHANA 001 | YORK | SBH 100 DW | 8,8 | 5.9 |  |  | 5.8 |  |  | 0.1 | 0 | 0 | 18.4 | 17.5 | 0.9 | 23.1 | 22.3 | 0.8 | 7 | 527 | 605 | 78 | 2922.15 | 3200 | 91.32% | NORMAL
279 | 2026-05-27 | RETAIL | L3 | PISC | BENIHANA 002 | YORK | SBH 100 DW | 8,8 | 6.1 |  |  | 6 |  |  | 0.1 | 0 | 0 | 19.7 | 18.3 | 1.4 | 23.4 | 22.4 | 1 | 7 | 516 | 594 | 78 | 2869.02 | 3200 | 89.66% | NORMAL
280 | 2026-05-27 | RETAIL | L3 | PISC | BENIHANA 003 | YORK | SBH 100 DW | 8,8 | 7.5 |  |  | 7.4 |  |  | 0.1 | 0 | 0 | 18.5 | 17.4 | 1.1 | 22.8 | 22.2 | 0.6 | 7 | 481 | 611 | 130 | 2951.13 | 3200 | 92.22% | NORMAL
281 | 2026-05-27 | RETAIL | L3 | PISC | BENIHANA 004 | YORK | SBH 100 DW | 8,8 | 7.6 |  |  | 7.5 |  |  | 0.1 | 0 | 0 | 18.2 | 17.2 | 1 | 22.7 | 22.1 | 0.6 | 7 | 491 | 600 | 109 | 2898 | 3200 | 90.56% | NORMAL
282 | 2026-05-27 | RETAIL | L3 | PISC | BENIHANA 005 | DAIKIN | DDB 100 BW | 7,4 | 6.6 |  |  | 6.5 |  |  | 0.1 | 0 | 0 | 18.5 | 16.8 | 1.7 | 22.7 | 22 | 0.7 | 7 | 441 | 621 | 180 | 2999.43 | 3200 | 93.73% | NORMAL
283 | 2026-05-27 | RETAIL | L3 | PISC | BIN HOUSE 001 | TRANE | HCCA 14 | 1.8 | 1.4 |  |  | 1.3 |  |  | 0.1 | 0 | 0 | 18.3 | 17.7 | 0.6 | 23.9 | 23.3 | 0.6 | 6 | 190 | 275 | 85 | 1138.5 | 1400 | 81.32% | NORMAL
284 | 2026-05-27 | RETAIL | L3 | PISC | BIN HOUSE 002 | TRANE | HCCA 18 | 2.8 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 18.6 | 18.1 | 0.5 | 23.6 | 23 | 0.6 | 6 | 333 | 370 | 37 | 1531.8 | 1800 | 85.1% | NORMAL
285 | 2026-05-27 | RETAIL | L3 | PISC | BIN HOUSE 003 | TRANE | HCCA 18 | 2.8 | 2.5 |  |  | 2.4 |  |  | 0.1 | 0 | 0 | 18.8 | 16.6 | 2.2 | 23.5 | 22.7 | 0.8 | 6 | 249 | 352 | 103 | 1457.28 | 1800 | 80.96% | NORMAL
286 | 2026-05-15 | RETAIL | L3 | PISC | MONDIAL 001 | DAIKIN | DDB 50 BW | 3.7 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 18.1 | 17.3 | 0.8 | 23.2 | 22 | 1.2 | 4 | 420 | 555 | 135 | 1531.8 | 1700 | 90.11% | NORMAL | - | -
287 | 2026-05-15 | RETAIL | L3 | PISC | MONDIAL 002 | TRANE | HCCA 18 | 2.9 | 1.8 |  |  | 1.5 |  |  | 0.3 | 0 | 0 | 19.2 | 17.4 | 1.8 | 22.8 | 22 | 0.8 | 4 | 394 | 558 | 164 | 1540.08 | 1800 | 85.56% | NORMAL | - | -
288 | 2026-05-15 | RETAIL | L3 | PISC | MONDIAL 003 | DAIKIN | DDB 40 BW | 3.43 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 18.6 | 17.8 | 0.8 | 23.5 | 22.7 | 0.8 | 4 | 254 | 372 | 118 | 1026.72 | 1250 | 82.14% | NORMAL | - | -
289 | 2026-05-16 | RETAIL | L3 | PISC | BAHA GIA 001 | DAIKIN | DDB 40 BW | 3.43 | 2.7 |  |  | 2.6 |  |  | 0.1 | 0 | 0 | 19.1 | 18.2 | 0.9 | 23.1 | 22 | 1.1 | 6 | 225 | 295 | 70 | 1221.3 | 1250 | 97.7% | NORMAL | - | -
290 | 2026-05-16 | RETAIL | L3 | PISC | BAHA GIA 002 | MC QUAY | MCC 40 | 1.8 | 1.2 |  |  | 1.1 |  |  | 0.1 | 0 | 0 | 18.6 | 17.8 | 0.8 | 22.8 | 22.2 | 0.6 | 6 | 213 | 328 | 115 | 1357.92 | 1500 | 90.53% | NORMAL | - | -
291 | 2026-05-16 | RETAIL | L3 | PISC | BAHA GIA 003 | DAIKIN | DDB 40 BW | 3.43 | 2.6 |  |  | 2.5 |  |  | 0.1 | 0 | 0 | 19.3 | 17.9 | 1.4 | 23.5 | 22.3 | 1.2 | 6 | 143 | 289 | 146 | 1196.46 | 1250 | 95.72% | NORMAL | - | -
292 | 2026-05-19 | RETAIL | L3 | PISC | ex. NATUZZI 001 | TRANE | HCCA 10 | 1.3 | 1.2 |  |  | 1.1 |  |  | 0.1 | 0 | 0 | 18.2 | 17.5 | 0.7 | 23.6 | 22.5 | 1.1 | 4 | 156 | 295 | 139 | 814.2 | 1000 | 81.42% | NORMAL | - | -
293 | 2026-05-19 | RETAIL | L3 | PISC | ex. NATUZZI 002 | YORK | SBH 100 DW | 8.8 | 7.7 |  |  | 7.6 |  |  | 0.1 | 0 | 0 | 19.3 | 17.1 | 2.2 | 22.4 | 21.5 | 0.9 | 6 | 424 | 620 | 196 | 2566.8 | 3200 | 80.21% | NORMAL | - | -
294 | 2026-05-19 | RETAIL | L3 | PISC | ex. NATUZZI 003 | MC QUAY | MCC 60 | 2.5 | 1.6 |  |  | 1.5 |  |  | 0.1 | 0 | 0 | 19.2 | 17.8 | 1.4 | 23 | 20.7 | 2.3 | 6 | 280 | 396 | 116 | 1639.44 | 2000 | 81.97% | NORMAL | - | -
295 | 2026-05-19 | RETAIL | L3 | PISC | ex. NATUZZI 004 | MC QUAY | MCC 60 | 2.5 | 2 |  |  | 1.8 |  |  | 0.2 | 0 | 0 | 18.1 | 17.4 | 0.7 | 23 | 22 | 1 | 6 | 290 | 430 | 140 | 1780.2 | 2000 | 89.01% | NORMAL | - | -
296 | 2026-05-20 | RETAIL | L3 | PISC | SEJAUH MATA MEMANDANG 001 | MC QUAY | MCC 50 | 2.3 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 20.2 | 17.5 | 2.7 | 23.4 | 22.6 | 0.8 | 6 | 212 | 340 | 128 | 1407.6 | 1750 | 80.43% | NORMAL
297 | 2026-05-20 | RETAIL | L3 | PISC | SEJAUH MATA MEMANDANG 002 | TRANE | HCCA 10 | 1.3 | 1.8 |  |  | 1.6 |  |  | 0.2 | 0 | 0 | 18.1 | 17.4 | 0.7 | 23 | 22 | 1 | 4 | 235 | 320 | 85 | 883.2 | 1000 | 88.32% | NORMAL
298 | 2026-05-20 | RETAIL | L3 | PISC | SEJAUH MATA MEMANDANG 003 | TRANE | HCCA 10 | 1.3 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 17.5 | 17 | 0.5 | 23.6 | 22.4 | 1.2 | 4 | 260 | 310 | 50 | 855.6 | 1000 | 85.56% | NORMAL
299 | 2026-05-14 | RETAIL | L3 | PISC | IWAN TIRTA 001 | MC QUAY | MCC 50 | 2,3 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 17.8 | 17.2 | 0.6 | 23.4 | 22.6 | 0.8 | 4 | 363 | 510 | 147 | 1407.6 | 1750 | 80.43% | NORMAL
300 | 2026-05-14 | RETAIL | L3 | PISC | IWAN TIRTA 002 | TRANE | HCCA 14 | 1.8 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 18.2 | 17.5 | 0.7 | 23.1 | 22.4 | 0.7 | 4 | 295 | 425 | 130 | 1173 | 1400 | 83.79% | NORMAL
301 | 2026-05-20 | RETAIL | L3 | PISC | STEFANO RICCI | TRANE | HCCA 24 | 4.9 | 2.2 |  |  | 2 |  |  | 0.2 | 0 | 0 | 17.6 | 17.2 | 0.4 | 22.8 | 22.1 | 0.7 | 5 | 460 | 600 | 140 | 2070 | 2400 | 86.25% | NORMAL | -
302 | 2026-05-22 | RETAIL | L3 | PISC | ELITE 001 | MC QUAY | MCC 60 | 2.5 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 19.6 | 17.5 | 2.1 | 22.7 | 22.1 | 0.6 | 5 | 228 | 493 | 265 | 1700.85 | 2000 | 85.04% | NORMAL
303 | 2026-05-22 | RETAIL | L3 | PISC | ELITE 002 | MC QUAY | MCC 50 | 2.3 | 2.2 |  |  | 2.1 |  |  | 0.1 | 0 | 0 | 19.8 | 17.4 | 2.4 | 22.7 | 22.2 | 0.5 | 5 | 397 | 444 | 47 | 1531.8 | 1750 | 87.53% | NORMAL
304 | 2026-05-19 | RETAIL | L3 | PISC | BILLSTONE | DAIKIN | DDB 75 BW | 3.4 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 18.2 | 17.6 | 0.6 | 22.3 | 21.8 | 0.5 | 6 | 400 | 570 | 170 | 2359.8 | 2500 | 94.39% | NORMAL | -
305 | 2026-05-28 | RETAIL | L3 | PISC | HAVANA GALLERY | DAIKIN | DDB 50 BW | 3.7 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 18.9 | 17.9 | 1 | 23 | 20.9 | 2.1 | 4 | 300 | 581 | 281 | 1603.56 | 1700 | 94.33% | NORMAL
306 | 2026-05-29 | RETAIL | L3 | PISC | D'ORSAY | DAIKIN | DDB 50 BW | 3.7 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 18.4 | 17.3 | 1.1 | 21.6 | 20.2 | 1.4 | 4 | 433 | 591 | 158 | 1631.16 | 1700 | 95.95% | NORMAL
307 | 2026-05-21 | RETAIL | L3 | PISC | JOHN FASHION 001 | TRANE | HCCA 10 | 1,3 | 0.6 |  |  | 0.5 |  |  | 0.1 | 0 | 0 | 18.6 | 17.8 | 0.8 | 22.7 | 22.1 | 0.6 | 4 | 117 | 295 | 178 | 814.2 | 1000 | 81.42% | NORMAL | -
308 | 2026-05-21 | RETAIL | L3 | PISC | JOHN FASHION 002 | YORK | SBH 40 DW | 3,6 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 17.3 | 16.4 | 0.9 | 22.8 | 22.2 | 0.6 | 4 | 254 | 372 | 118 | 1026.72 | 1250 | 82.14% | NORMAL | -
309 | 2026-05-21 | RETAIL | L3 | PISC | JOHN FASHION 003 | TRANE | HCCA 10 | 1,3 | 0.7 |  |  | 0.5 |  |  | 0.2 | 0 | 0 | 20.1 | 18.6 | 1.5 | 22.9 | 21.8 | 1.1 | 4 | 189 | 312 | 123 | 861.12 | 1000 | 86.11% | NORMAL | -
310 | 2026-05-23 | RETAIL | L3 | PISC | JOHN FASHION 004 | TRANE | HCCA 10 | 1,3 | 0.9 |  |  | 0.7 |  |  | 0.2 | 0 | 0 | 19.6 | 18.5 | 1.1 | 23.8 | 22.7 | 1.1 | 4 | 125 | 295 | 170 | 814.2 | 1000 | 81.42% | NORMAL | -
311 | 2026-05-23 | RETAIL | L3 | PISC | JOHN FASHION 005 | TRANE | HCCA 10 | 1,3 | 1.2 |  |  | 0.9 |  |  | 0.3 | 0 | 0 | 19.3 | 17.9 | 1.4 | 23.1 | 22 | 1.1 | 4 | 143 | 299 | 156 | 825.24 | 1000 | 82.52% | NORMAL | -
312 | 2026-05-29 | RETAIL | L3 | PISC | NUDIE JEANS CO 001 | TRANE | HCCA 18 | 2.9 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 18.2 | 17.6 | 0.6 | 22.8 | 22.1 | 0.7 | 4 | 449 | 565 | 116 | 1559.4 | 1800 | 86.63% | NORMAL
313 | 2026-05-29 | RETAIL | L3 | PISC | NUDIE JEANS CO 002 | TRANE | HCCA 18 | 2.9 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 17 | 16.7 | 0.3 | 22.7 | 21.9 | 0.8 | 4 | 457 | 528 | 71 | 1457.28 | 1800 | 80.96% | NORMAL
314 | 2026-05-29 | RETAIL | L3 | PISC | NUDIE JEANS CO 003 | TRANE | HCCA 18 | 2.9 | 1.1 |  |  | 0.9 |  |  | 0.2 | 0 | 0 | 17.1 | 16.2 | 0.9 | 23.1 | 21.8 | 1.3 | 4 | 477 | 555 | 78 | 1531.8 | 1800 | 85.1% | NORMAL
315 | 2026-05-21 | RETAIL | L3 | PISC | LACOSTE 001 | MC QUAY | MCC 60 | 2.5 | 2 |  |  | 1.8 |  |  | 0.2 | 0 | 0 | 17.3 | 16.4 | 0.9 | 22.8 | 22 | 0.8 | 5 | 275 | 465 | 190 | 1604.25 | 2000 | 80.21% | NORMAL | -
316 | 2026-05-21 | RETAIL | L3 | PISC | LACOSTE 002 | DAIKIN | DDB 50 BW | 3.7 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 18.3 | 17.7 | 0.6 | 22.9 | 21.1 | 1.8 | 5 | 375 | 455 | 80 | 1569.75 | 1700 | 92.34% | NORMAL | -
317 | 2026-05-21 | RETAIL | L3 | PISC | LACOSTE 003 | DAIKIN | DDB 50 BW | 3.7 | 3 |  |  | 2.9 |  |  | 0.1 | 0 | 0 | 18.6 | 18.1 | 0.5 | 22.8 | 22 | 0.8 | 5 | 348 | 460 | 112 | 1587 | 1700 | 93.35% | NORMAL | -
318 | 2026-05-16 | RETAIL | L3 | PISC | CROWN JEWELLERY | TRANE | HCCA 18 | 2,9 | 1.4 |  |  | 1.2 |  |  | 0.2 | 0 | 0 | 19.1 | 17.1 | 2 | 22.7 | 22.1 | 0.6 | 6 | 236 | 349 | 113 | 1444.86 | 1800 | 80.27% | NORMAL
319 | 2026-05-16 | RETAIL | L3 | PISC | BENTENG JEWELLERY | TRANE | HCCA 14 | 1,8 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 17 | 16.3 | 0.7 | 23.4 | 22.4 | 1 | 6 | 192 | 278 | 86 | 1150.92 | 1400 | 82.21% | NORMAL
320 | 2026-05-26 | RETAIL | L3 | PISC | ON JAKARTA 001 | TRANE | HCCA 18 | 2.9 | 2.1 |  |  | 1.9 |  |  | 0.2 | 0 | 0 | 18.3 | 17.7 | 0.6 | 23.4 | 22.6 | 0.8 | 4 | 463 | 540 | 77 | 1490.4 | 1800 | 82.8% | NORMAL
321 | 2026-05-26 | RETAIL | L3 | PISC | ON JAKARTA 002 | TRANE | HCCA 18 | 2,9 | 2.4 |  |  | 2.3 |  |  | 0.1 | 0 | 0 | 18.6 | 18.1 | 0.5 | 23.1 | 22.4 | 0.7 | 4 | 395 | 525 | 130 | 1449 | 1800 | 80.5% | NORMAL
322 | 2026-05-26 | RETAIL | L3 | PISC | ON JAKARTA 003 | MC QUAY | MCC 60 | 2.5 | 2.2 |  |  | 2 |  |  | 0.2 | 0 | 0 | 18.8 | 16.6 | 2.2 | 23.2 | 22.4 | 0.8 | 4 | 462 | 608 | 146 | 1678.08 | 2000 | 83.9% | NORMAL
323 | 2026-05-26 | RETAIL | L3 | PISC | ON JAKARTA 004 | TRANE | HCCA 14 | 1.8 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 18.2 | 17.5 | 0.7 | 23.4 | 22.6 | 0.8 | 4 | 335 | 440 | 105 | 1214.4 | 1400 | 86.74% | NORMAL
324 | 2026-05-26 | RETAIL | L3 | PISC | ON JAKARTA 005 | MC QUAY | MCC 50 | 2.3 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 19.3 | 17.1 | 2.2 | 23 | 22 | 1 | 4 | 360 | 510 | 150 | 1407.6 | 1750 | 80.43% | NORMAL
325 | 2026-05-28 | RETAIL | L3 | PISC | WANDA HOUSE OF JEWELS | MC QUAY | MCC 50 | 2.3 | 1.7 |  |  | 1.6 |  |  | 0.1 | 0 | 0 | 17 | 16.7 | 0.3 | 22.9 | 22.3 | 0.6 | 6 | 204 | 345 | 141 | 1428.3 | 1750 | 81.62% | NORMAL
326 | 2026-05-31 | RETAIL | L3 | PISC | PRESTIGE JEWELLERY | TRANE | HCCA 18 | 2.9 | 1.7 |  |  | 1.8 |  |  | -0.1 | 0 | 0 | 18.6 | 16.8 | 1.8 | 23.3 | 21.9 | 1.4 | 5 | 250 | 430 | 180 | 1483.5 | 1800 | 82.42% | NORMAL
327 | 2026-05-17 | RETAIL | L3 | PISC | CALVIN KLEIN 001 | MC QUAY | MCC 60 | 2.5 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 18.9 | 17.8 | 1.1 | 23.4 | 22.9 | 0.5 | 6 | 290 | 410 | 120 | 1697.4 | 2000 | 84.87% | NORMAL | -
328 | 2026-05-17 | RETAIL | L3 | PISC | CALVIN KLEIN 002 | MC QUAY | MCC 50 | 2.3 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 18.6 | 17.2 | 1.4 | 23.5 | 22.6 | 0.9 | 6 | 269 | 370 | 101 | 1531.8 | 1750 | 87.53% | NORMAL | -
329 | 2026-05-28 | RETAIL | L3 | PISC | REGAL JEWELS | MC QUAY | MCC 60 | 2.5 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 18.9 | 16.9 | 2 | 23 | 21 | 2 | 5 | 380 | 490 | 110 | 1690.5 | 2000 | 84.52% | NORMAL
330 | 2026-05-21 | RETAIL | L3 | PISC | MULIA JEWELLERY | MCQUAY | MCC 60 | 2.5 | 1.7 |  |  | 1.6 |  |  | 0.1 | 0 | 0 | 19.6 | 18.8 | 0.8 | 22.9 | 21.8 | 1.1 | 6 | 325 | 414 | 89 | 1713.96 | 2000 | 85.7% | NORMAL | -
331 | 2026-05-16 | RETAIL | L3 | PISC | L'OCCITANE | MC QUAY | MCC 60 | 2.5 | 1.9 |  |  | 1.7 |  |  | 0.2 | 0 | 0 | 17.3 | 16.1 | 1.2 | 22.4 | 21.2 | 1.2 | 4 | 455 | 590 | 135 | 1628.4 | 2000 | 81.42% | NORMAL
332 | 2026-05-24 | RETAIL | L3 | PISC | OSIM 002 | MC QUAY | MCC 60 | 2,5 | 1.6 |  |  | 1.4 |  |  | 0.2 | 0 | 0 | 17.3 | 16.5 | 0.8 | 22.7 | 21.9 | 0.8 | 4 | 452 | 629 | 177 | 1736.04 | 2000 | 86.8% | NORMAL
333 | 2026-05-24 | RETAIL | L3 | PISC | OSIM 003 | MC QUAY | MCC 60 | 2,5 | 2.4 |  |  | 2.3 |  |  | 0.1 | 0 | 0 | 18.2 | 17 | 1.2 | 22.6 | 21.8 | 0.8 | 4 | 410 | 610 | 200 | 1683.6 | 2000 | 84.18% | NORMAL
334 | 2026-05-17 | RETAIL | L3 | PISC | ADELLE JEWELLERY | TRANE | HCCA 24 | 4.9 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 17 | 16.3 | 0.7 | 22.7 | 22.1 | 0.6 | 6 | 336 | 484 | 148 | 2003.76 | 2400 | 83.49% | NORMAL
335 | 2026-05-21 | RETAIL | L3 | PISC | MELISSA 001 | DAIKIN | DDB 50 BW | 3.7 | 2.5 |  |  | 2.3 |  |  | 0.2 | 0 | 0 | 18.3 | 17.8 | 0.5 | 22.9 | 22.4 | 0.5 | 6 | 235 | 390 | 155 | 1614.6 | 1700 | 94.98% | NORMAL | -
336 | 2026-05-21 | RETAIL | L3 | PISC | MELISSA 002 | MC QUAY | MCC 60 | 2,5 | 1.7 |  |  | 1.5 |  |  | 0.2 | 0 | 0 | 19.5 | 17.2 | 2.3 | 22.7 | 21.9 | 0.8 | 6 | 292 | 387 | 95 | 1602.18 | 2000 | 80.11% | NORMAL | -
337 | 2026-05-17 | F&B | L3 | PISC | DORE | MC QUAY | MCC 60 | 2.5 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 18.6 | 18.1 | 0.5 | 23.4 | 22.4 | 1 | 6 | 274 | 394 | 120 | 1631.16 | 2000 | 81.56% | NORMAL | -
338 | 2026-05-23 | RETAIL | L3 | PISC | SWAROVSKI | MC QUAY | MCC 50 | 2.3 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 18.6 | 17.3 | 1.3 | 22.8 | 21.3 | 1.5 | 6 | 240 | 345 | 105 | 1428.3 | 1750 | 81.62% | NORMAL
339 | 2026-05-15 | RETAIL | L3 | PISC | TULOLA 001 | MC QUAY | MCC 60 | 2.5 | 2.2 |  |  | 2.1 |  |  | 0.1 | 0 | 0 | 18.7 | 17.6 | 1.1 | 22.5 | 21.6 | 0.9 | 5 | 410 | 476 | 66 | 1642.2 | 2000 | 82.11% | NORMAL
340 | 2026-05-15 | RETAIL | L3 | PISC | TULOLA 002 | TRANE | HCCA 10 | 1.3 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 18.6 | 17.3 | 1.3 | 22.8 | 21.3 | 1.5 | 5 | 125 | 246 | 121 | 848.7 | 1000 | 84.87% | NORMAL
341 | 2026-05-24 | BOH | L3 | PISC | TOILET N | MC QUAY | MCC 50 | 2.3 | 1.5 |  |  | 1.3 |  |  | 0.2 | 0 | 0 | 19.2 | 16.7 | 2.5 | 23.8 | 22.7 | 1.1 | 6 | 245 | 360 | 115 | 1490.4 | 1750 | 85.17% | NORMAL
342 | 2026-05-24 | BOH | L3 | PISC | CORRIDOR LIFT 1-2 | ITU | 1200 | 0.7 | 0.4 |  |  | 0.3 |  |  | 0.1 | 0 | 0 | 19.6 | 18.8 | 0.8 | 23.5 | 22.7 | 0.8 | 4 | 241 | 348 | 107 | 960.48 | 1200 | 80.04% | NORMAL
343 | 2026-05-24 | RETAIL | L3 | PISC | ROYAL SELANGOR | YORK | SBH 60 DW | 6,3 | 5.6 |  |  | 5.4 |  |  | 0.2 | 0 | 0 | 19.6 | 16.7 | 2.9 | 22.9 | 22.3 | 0.6 | 7 | 297 | 487 | 190 | 2352.21 | 2500 | 94.09% | NORMAL
344 | 2026-05-16 | SALON | L4 | PISC | PETER F. SAERANG | TRANE | HCCA 24 | 4.9 | 3 |  |  | 2.7 |  |  | 0.3 | 0 | 0 | 19.8 | 17.8 | 2 | 22.9 | 21.3 | 1.6 | 7 | 389 | 420 | 31 | 2028.6 | 2400 | 84.52% | NORMAL
345 | 2026-05-30 | F&B | L4 | PISC | SAMWON GARDEN 01 | YORK | SBH 75 DW | 6,3 | 3.7 |  |  | 3.6 |  |  | 0.1 | 0 | 0 | 19.4 | 17.2 | 2.2 | 22.6 | 22 | 0.6 | 5 | 304 | 589 | 285 | 2032.05 | 2500 | 81.28% | NORMAL
346 | 2026-05-30 | F&B | L4 | PISC | SAMWON GARDEN 02 | YORK | SBH 60 DW | 6.3 | 4.5 |  |  | 4.4 |  |  | 0.1 | 0 | 0 | 19.5 | 17.2 | 2.3 | 22.8 | 22.1 | 0.7 | 7 | 307 | 432 | 125 | 2086.56 | 2500 | 83.46% | NORMAL
347 | 2026-05-30 | F&B | L4 | PISC | SAMWON GARDEN 03 | TRANE | HCCA 24 | 4,9 | 3.9 |  |  | 3.8 |  |  | 0.1 | 0 | 0 | 18.7 | 18 | 0.7 | 23.7 | 22 | 1.7 | 5 | 292 | 565 | 273 | 1949.25 | 2400 | 81.22% | NORMAL
348 | 2026-05-30 | F&B | L4 | PISC | SAMWON GARDEN 04 | TRANE | HCCA 24 | 4.9 | 3.8 |  |  | 3.7 |  |  | 0.1 | 0 | 0 | 18.9 | 17 | 1.9 | 23.5 | 22 | 1.5 | 5 | 415 | 557 | 142 | 1921.65 | 2400 | 80.07% | NORMAL
349 | 2026-05-30 | F&B | L4 | PISC | GYUKAKU PRIME 001 | TRANE | HCCA 24 | 4.9 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 17.2 | 16.8 | 0.4 | 23 | 21.6 | 1.4 | 8 | 200 | 370 | 170 | 2042.4 | 2400 | 85.1% | NORMAL
350 | 2026-05-30 | F&B | L4 | PISC | GYUKAKU PRIME 002 | TRANE | HCCA 24 | 4.9 | 3.5 |  |  | 3.4 |  |  | 0.1 | 0 | 0 | 17 | 16.6 | 0.4 | 23 | 21.2 | 1.8 | 8 | 230 | 350 | 120 | 1932 | 2400 | 80.5% | NORMAL
351 | 2026-05-30 | F&B | L4 | PISC | GYUKAKU PRIME 003 | YORK | SBH 125 DW | 3.7 | 3.8 |  |  | 3.7 |  |  | 0.1 | 0 | 0 | 18 | 17.3 | 0.7 | 23 | 21.6 | 1.4 | 6 | 700 | 870 | 170 | 3601.8 | 4100 | 87.85% | NORMAL
352 | 2026-05-29 | F&B | L4 | PISC | LAPIS-LAPIS | TRANE | HCCA 24 | 4.9 | 2.4 |  |  | 2.3 |  |  | 0.1 | 0 | 0 | 19.5 | 17.4 | 2.1 | 22.5 | 21.4 | 1.1 | 6 | 327 | 481 | 154 | 1991.34 | 2400 | 82.97% | NORMAL
353 | 2026-05-25 | F&B | L4 | PISC | KAM'S ROAST 001 | YORK | SBH 125 DW | 3.7 | 4.5 |  |  | 4.4 |  |  | 0.1 | 0 | 0 | 19.5 | 17.2 | 2.3 | 22.8 | 22.1 | 0.7 | 7 | 607 | 732 | 125 | 3535.56 | 4100 | 86.23% | NORMAL
354 | 2026-05-25 | F&B | L4 | PISC | KAM'S ROAST 002 | TRANE | HCCA 24 | 4.9 | 2.8 |  |  | 2.7 |  |  | 0.1 | 0 | 0 | 18.7 | 18 | 0.7 | 23 | 22.1 | 0.9 | 5 | 540 | 615 | 75 | 2121.75 | 2400 | 88.41% | NORMAL
355 | 2026-05-25 | BOH | L4 | PISC | CORRIDOR KAM'S ROAST 001 | TRANE | HCCA 24 | 4.9 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 19.6 | 18 | 1.6 | 23.9 | 22.3 | 1.6 | 7 | 293 | 425 | 132 | 2052.75 | 2400 | 85.53% | NORMAL
356 | 2026-05-25 | BOH | L4 | PISC | CORRIDOR KAM'S ROAST 002 | TRANE | HCCA 24 | 4.9 | 2.7 |  |  | 2.6 |  |  | 0.1 | 0 | 0 | 19.1 | 18.4 | 0.7 | 24.1 | 23 | 1.1 | 7 | 291 | 402 | 111 | 1941.66 | 2400 | 80.9% | NORMAL
357 | 2026-05-23 | SALON | L4 | PISC | BMF CLINIC - THE AESTHETICS 001 | TRANE | HCCA 24 | 4.9 | 3.8 |  |  | 3.7 |  |  | 0.1 | 0 | 0 | 17 | 16.7 | 0.3 | 22.9 | 22 | 0.9 | 5 | 475 | 595 | 120 | 2052.75 | 2400 | 85.53% | NORMAL
358 | 2026-05-23 | SALON | L4 | PISC | BMF CLINIC - THE AESTHETICS 002 | TRANE | HCCA 24 | 4.9 | 3.2 |  |  | 3.1 |  |  | 0.1 | 0 | 0 | 17.1 | 16.2 | 0.9 | 23.1 | 22.2 | 0.9 | 5 | 379 | 559 | 180 | 1928.55 | 2400 | 80.36% | NORMAL
359 | 2026-05-25 | SALON | L4 | PISC | J BIOLETTI BY PARLOUR 01 | YORK | SBH 125 | 8 | 6.3 |  |  | 6.2 |  |  | 0.1 | 0 | 0 | 17.8 | 17.2 | 0.6 | 22 | 21.1 | 0.9 | 6 | 307 | 514 | 207 | 2127.96 | 2400 | 88.67% | NORMAL
360 | 2026-05-25 | SALON | L4 | PISC | J BIOLETTI BY PARLOUR 02 | TRANE | HCCA 10 | 1.3 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 17.5 | 17 | 0.5 | 21.5 | 20.4 | 1.1 | 6 | 301 | 507 | 206 | 2098.98 | 2400 | 87.46% | NORMAL
361 | 2026-05-25 | SALON | L4 | PISC | J BIOLETTI BY PARLOUR 03 | TRANE | HCCA 24 | 3,7 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 18 | 17.5 | 0.5 | 22.9 | 21.3 | 1.6 | 6 | 807 | 912 | 105 | 3775.68 | 4100 | 92.09% | NORMAL
362 | 2026-05-26 | SALON | L4 | PISC | LIFE HOUSE | TRANE | HCCA 24 | 4.9 | 3.8 |  |  | 3.7 |  |  | 0.1 | 0 | 0 | 18.9 | 17 | 1.9 | 23.5 | 22 | 1.5 | 6 | 315 | 467 | 152 | 1933.38 | 2400 | 80.56% | NORMAL
363 | 2026-05-21 | SALON | L4 | PISC | HOUSE OF ULTIMA II 001 | YORK | SBH 30 | 1.9 | 1.4 |  |  | 1.3 |  |  | 0.1 | 0 | 0 | 17.2 | 16.9 | 0.3 | 22.7 | 22.2 | 0.5 | 3 | 285 | 405 | 120 | 838.35 | 1000 | 83.83% | NORMAL
364 | 2026-05-21 | SALON | L4 | PISC | HOUSE OF ULTIMA II 002 | TRANE | HCCA 24 | 4.9 | 2.3 |  |  | 2.1 |  |  | 0.2 | 0 | 0 | 17.5 | 16.8 | 0.7 | 22.6 | 22 | 0.6 | 6 | 300 | 495 | 195 | 2049.3 | 2400 | 85.39% | NORMAL
365 | 2026-05-23 | SALON | L4 | PISC | EVERLASH | TRANE | HCCA 24 | 4.9 | 3.6 |  |  | 3.5 |  |  | 0.1 | 0 | 0 | 18.4 | 16.5 | 1.9 | 22.9 | 22.1 | 0.8 | 6 | 314 | 506 | 192 | 2094.84 | 2400 | 87.28% | NORMAL
366 | 2026-05-20 | SALON | L4 | PISC | DE SALON 001 | TRANE | HCCA 24 | 4.9 | 4.5 |  |  | 4.2 |  |  | 0.3 | 0 | 0 | 19.4 | 17.2 | 2.2 | 23.1 | 22 | 1.1 | 8 | 231 | 360 | 129 | 1987.2 | 2400 | 82.8% | NORMAL
367 | 2026-05-20 | SALON | L4 | PISC | DE SALON 002 | YORK | SBH 40 DW | 3.6 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 18.4 | 16.5 | 1.9 | 23.5 | 21.6 | 1.9 | 4 | 214 | 374 | 160 | 1032.24 | 1250 | 82.58% | NORMAL
368 | 2026-05-26 | SALON | L4 | PISC | LAVALEN 01 | TRANE | HCCA 24 | 4.9 | 3.8 |  |  | 3.6 |  |  | 0.2 | 0 | 0 | 18.2 | 16.9 | 1.3 | 23.3 | 21.9 | 1.4 | 7 | 300 | 401 | 101 | 1936.83 | 2400 | 80.7% | NORMAL
369 | 2026-05-26 | SALON | L4 | PISC | LAVALEN 02 | TRANE | HCCA 24 | 4.9 | 1.8 |  |  | 1.3 |  |  | 0.5 | 0 | 0 | 19.7 | 18.8 | 0.9 | 23.6 | 22.5 | 1.1 | 7 | 271 | 399 | 128 | 1927.17 | 2400 | 80.3% | NORMAL
370 | 2026-05-26 | SALON | L4 | PISC | LAVALEN 03 | TRANE | HCCA 24 | 4.9 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 18.5 | 17.4 | 1.1 | 22.9 | 22 | 0.9 | 6 | 351 | 490 | 139 | 2028.6 | 2400 | 84.52% | NORMAL
371 | 2026-05-26 | SALON | L4 | PISC | LAVALEN 04 | TRANE | HCCA 24 | 4.9 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 19.5 | 16.4 | 3.1 | 22.7 | 22.2 | 0.5 | 6 | 291 | 489 | 198 | 2024.46 | 2400 | 84.35% | NORMAL
372 | 2026-05-28 | SALON | L4 | PISC | HAIRTITUDE | TRANE | HCCA 24 | 4.9 | 3.7 |  |  | 3.4 |  |  | 0.3 | 0 | 0 | 19 | 16.9 | 2.1 | 23.3 | 20.9 | 2.4 | 7 | 285 | 400 | 115 | 1932 | 2400 | 80.5% | NORMAL
373 | 2026-05-28 | SALON | L4 | PISC | BENTENG JEWELLERY | TRANE | HCCA 24 | 4.9 | 3.2 |  |  | 3.1 |  |  | 0.1 | 0 | 0 | 18 | 17.9 | 0.1 | 23 | 22.5 | 0.5 | 5 | 379 | 559 | 180 | 1928.55 | 2400 | 80.36% | NORMAL
374 | 2026-05-26 | RETAIL | L4 | PISC | PENINSULA | YORK | SBH 30 DW | 1.9 | 1.4 |  |  | 1.3 |  |  | 0.1 | 0 | 0 | 18.7 | 18 | 0.7 | 22.6 | 21.7 | 0.9 | 4 | 184 | 305 | 121 | 841.8 | 1000 | 84.18% | NORMAL
375 | 2026-05-24 | RETAIL | L4 | PISC | NOBU 001 | YORK | SBH 60 DW | 6,3 | 5.3 |  |  | 5.2 |  |  | 0.1 | 0 | 0 | 17.8 | 17.2 | 0.6 | 22.5 | 21.4 | 1.1 | 5 | 492 | 655 | 163 | 2259.75 | 2500 | 90.39% | NORMAL
376 | 2026-05-24 | RETAIL | L4 | PISC | NOBU 002 | YORK | SBH 30 DW | 1,9 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 17.5 | 17 | 0.5 | 22.4 | 20.6 | 1.8 | 5 | 117 | 250 | 133 | 862.5 | 1000 | 86.25% | NORMAL
377 | 2026-05-26 | SALON | L4 | PISC | BODIES | YORK | SBH 30 DW | 1.9 | 1.5 |  |  | 1.2 |  |  | 0.3 | 0 | 0 | 19.7 | 17.5 | 2.2 | 23.1 | 21.7 | 1.4 | 3 | 285 | 390 | 105 | 807.3 | 1000 | 80.73% | NORMAL
378 | 2026-05-25 | RETAIL | L4 | PISC | BATIK KERIS 001 | MC QUAY | MCC 60 | 2.5 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 19 | 18.7 | 0.3 | 23.9 | 22.3 | 1.6 | 4 | 494 | 615 | 121 | 1697.4 | 2000 | 84.87% | NORMAL
379 | 2026-05-25 | RETAIL | L4 | PISC | BATIK KERIS 002 | MC QUAY | MCC 60 | 2.5 | 1.8 |  |  | 1.6 |  |  | 0.2 | 0 | 0 | 19.7 | 18 | 1.7 | 24.1 | 23 | 1.1 | 4 | 415 | 595 | 180 | 1642.2 | 2000 | 82.11% | NORMAL
380 | 2026-05-25 | RETAIL | L4 | PISC | BATIK KERIS 003 | MC QUAY | MCC 60 | 2.5 | 2 |  |  | 1.9 |  |  | 0.1 | 0 | 0 | 19.5 | 18.4 | 1.1 | 22.4 | 21.2 | 1.2 | 4 | 420 | 610 | 190 | 1683.6 | 2000 | 84.18% | NORMAL
381 | 2026-05-29 | RETAIL | L4 | PISC | OEMAH ETNIK | DAIKIN | DDB 60 BW | 3,4 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 18.3 | 16.2 | 2.1 | 23 | 21.2 | 1.8 | 4 | 600 | 701 | 101 | 1934.76 | 2150 | 89.99% | NORMAL
382 | 2026-05-29 | RETAIL | L4 | PISC | VIVAIA | YORK | SBH 125 DW | 3,7 | 3.1 |  |  | 3 |  |  | 0.1 | 0 | 0 | 18 | 16.7 | 1.3 | 23.1 | 22 | 1.1 | 7 | 550 | 720 | 170 | 3477.6 | 4100 | 84.82% | NORMAL
383 | 2026-05-29 | RETAIL | L4 | PISC | JOSEPHINE ANNI | DAIKIN | DDB 60 BW | 3,4 | 2.6 |  |  | 2.4 |  |  | 0.2 | 0 | 0 | 17.3 | 16.9 | 0.4 | 22.2 | 21.5 | 0.7 | 6 | 321 | 490 | 169 | 2028.6 | 2150 | 94.35% | NORMAL
384 | 2026-05-28 | RETAIL | L4 | PISC | LUVAZE | DAIKIN | DDB 60 BW | 3,4 | 3.2 |  |  | 3.1 |  |  | 0.1 | 0 | 0 | 18.2 | 17.6 | 0.6 | 23.4 | 22.6 | 0.8 | 6 | 304 | 471 | 167 | 1949.94 | 2150 | 90.69% | NORMAL
385 | 2026-05-28 | RETAIL | L4 | PISC | CIEL | DAIKIN | DDB 60 BW | 3.4 | 3.2 |  |  | 3.1 |  |  | 0.1 | 0 | 0 | 18.2 | 17.6 | 0.6 | 23.3 | 21.9 | 1.4 | 5 | 410 | 590 | 180 | 2035.5 | 2150 | 94.67% | NORMAL
386 | 2026-05-28 | RETAIL | L4 | PIE | ARRAY OFF DAY | YORK | SBH 100 DW | 8.8 | 7.6 |  |  | 7.5 |  |  | 0.1 | 0 | 0 | 17.5 | 17 | 0.5 | 22.5 | 21.7 | 0.8 | 5 | 610 | 780 | 170 | 2691 | 3200 | 84.09% | NORMAL
387 | 2026-05-28 | BOH | L4 | PIE | R. MAKE UP ARTIS | TRANE | HFCA 12 | 1,2 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 18 | 17.5 | 0.5 | 22.5 | 21.7 | 0.8 | 4 | 230 | 350 | 120 | 966 | 1200 | 80.5% | NORMAL
388 | 2026-05-25 | BOH | L4 | PISC | TOILET SW | TRANE | HCCA 24 | 4.9 | 2.3 |  |  | 2.2 |  |  | 0.1 | 0 | 0 | 18.7 | 17.2 | 1.5 | 23.6 | 22.4 | 1.2 | 7 | 275 | 400 | 125 | 1932 | 2400 | 80.5% | NORMAL
389 | 2026-05-01 | BOH | L4 | PISC | R. ENGINEERING | YORK | SBH 75 DW | 6,3 | 5.3 |  |  | 4.9 |  |  | 0.4 | 0 | 0 | 19.3 | 18.7 | 0.6 | 23 | 22.1 | 0.9 | 8 | 305 | 387 | 82 | 2136.24 | 2500 | 85.45% | NORMAL
390 | 2026-05-01 | BOH | L4 | PISC | OFFICE JAYA KENCANA | MC QUAY | MCC 50 | 2.3 | 1.9 |  |  | 1.7 |  |  | 0.2 | 0 | 0 | 18.3 | 17.6 | 0.7 | 22.9 | 22.3 | 0.6 | 6 | 210 | 350 | 140 | 1449 | 1750 | 82.8% | NORMAL
391 | 2026-05-01 | BOH | L4 | PISC | R. PANEL 001 | ITU | 1200 | 0.7 | 0.6 |  |  | 0.5 |  |  | 0.1 | 0 | 0 | 18.3 | 17.6 | 0.7 | 22.9 | 22.6 | 0.3 | 4 | 215 | 350 | 135 | 966 | 1200 | 80.5% | NORMAL
392 | 2026-05-01 | BOH | L4 | PISC | R. PANEL 002 | ITU | 1200 | 0.7 | 0.5 |  |  | 0.4 |  |  | 0.1 | 0 | 0 | 18.5 | 17.7 | 0.8 | 24.2 | 23.5 | 0.7 | 4 | 255 | 350 | 95 | 966 | 1200 | 80.5% | NORMAL
393 | 2026-05-01 | BOH | L4 | PISC | R. PANEL 003 | MC QUAY | MCC 60 | 2.5 | 1.9 |  |  | 1.7 |  |  | 0.2 | 0 | 0 | 17.5 | 16.8 | 0.7 | 22.8 | 22.5 | 0.3 | 4 | 440 | 582 | 142 | 1606.32 | 2000 | 80.32% | NORMAL
394 | 2026-05-01 | BOH | L4 | PISC | R. PANEL 004 | MC QUAY | MCC 60 | 2.5 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 18.1 | 17.4 | 0.7 | 23.4 | 22.9 | 0.5 | 4 | 455 | 603 | 148 | 1664.28 | 2000 | 83.21% | NORMAL
395 | 2026-05-15 | BOH | L5 | PISC | R. CHILLER | YORK | SBH 75 DW | 6,3 | 4.9 |  |  | 4.3 |  |  | 0.6 | 0 | 0 | 17.8 | 17.2 | 0.6 | 23.6 | 22.8 | 0.8 | 5 | 435 | 590 | 155 | 2035.5 | 2500 | 81.42% | NORMAL
396 | 2026-05-01 | BOH | P1 | PISC | R. MDF 001 | ITU | 1200 | 0.7 | 0.4 |  |  | 0.3 |  |  | 0.1 | 0 | 0 | 19.4 | 17.2 | 2.2 | 22.6 | 22 | 0.6 | 4 | 259 | 300 | 41 | 828 | 1000 | 82.8% | NORMAL
397 | 2026-05-01 | BOH | P1 | PISC | R. MDF 002 | MC QUAY | MCC 30 | 1,9 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 19.1 | 17.9 | 1.2 | 23.1 | 22.7 | 0.4 | 4 | 168 | 291 | 123 | 803.16 | 1000 | 80.32% | NORMAL
398 | 2026-05-30 | BOH | P1 | PISC | ESCALATOR TIMUR 001 | AICOOL | FC 24 | 0.9 | 0.5 |  |  | 0.3 |  |  | 0.2 | 0 | 0 | 19.6 | 18.8 | 0.8 | 23 | 22.8 | 0.2 | 4 | 180 | 300 | 120 | 828 | 1000 | 82.8% | NORMAL
399 | 2026-05-30 | BOH | P1 | PISC | ESCALATOR TIMUR 002 | AICOOL | FC 24 | 0.9 | 0.5 |  |  | 0.3 |  |  | 0.2 | 0 | 0 | 19.5 | 18.8 | 0.7 | 23.1 | 22.8 | 0.3 | 4 | 118 | 290 | 172 | 800.4 | 1000 | 80.04% | NORMAL
400 | 2026-05-30 | BOH | P2 | PISC | TRASHROOM 01 | MC QUAY | MCC 60 | 2.5 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 18.8 | 17.7 | 1.1 | 22.6 | 22 | 0.6 | 4 | 278 | 599 | 321 | 1653.24 | 2000 | 82.66% | NORMAL
401 | 2026-05-30 | BOH | P2 | PISC | TRASHROOM 02 | MC QUAY | MCC 60 | 2.5 | 1.9 |  |  | 1.8 |  |  | 0.1 | 0 | 0 | 17.1 | 16.2 | 0.9 | 22.7 | 21 | 1.7 | 4 | 493 | 580 | 87 | 1600.8 | 2000 | 80.04% | NORMAL
402 | 2026-05-27 | BOH | P2 | PISC | MASJID BAITURRAHMAN 001 | TRANE | HCCA 18 | 2,9 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 17.3 | 16.2 | 1.1 | 23.1 | 22.7 | 0.4 | 4 | 330 | 530 | 200 | 1462.8 | 1800 | 81.27% | NORMAL
403 | 2026-05-27 | BOH | P2 | PISC | MASJID BAITURRAHMAN 002 | ITU | 1200 | 0,7 | 0.5 |  |  | 0.4 |  |  | 0.1 | 0 | 0 | 17.3 | 16.2 | 1.1 | 23 | 22.1 | 0.9 | 4 | 120 | 290 | 170 | 800.4 | 1000 | 80.04% | NORMAL
404 | 2026-05-27 | BOH | P2 | PISC | MASJID BAITURRAHMAN 003 | TRANE | HCCA 24 | 4.9 | 4 |  |  | 3.9 |  |  | 0.1 | 0 | 0 | 18.2 | 16 | 2.2 | 23.5 | 22.9 | 0.6 | 6 | 330 | 475 | 145 | 1966.5 | 2400 | 81.94% | NORMAL
405 | 2026-05-27 | BOH | P2 | PISC | MASJID BAITURRAHMAN 004 | TRANE | HCCA 24 | 4.9 | 3.3 |  |  | 3.2 |  |  | 0.1 | 0 | 0 | 18 | 16.5 | 1.5 | 23.2 | 23 | 0.2 | 6 | 325 | 485 | 160 | 2007.9 | 2400 | 83.66% | NORMAL
406 | 2026-05-27 | BOH | P2 | PISC | MASJID BAITURRAHMAN 005 | DAIKIN | FWW 1800 | 2.69 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 18.2 | 17.8 | 0.4 | 22.8 | 21.5 | 1.3 | 5 | 356 | 478 | 122 | 1649.1 | 1800 | 91.62% | NORMAL
407 | 2026-05-28 | BOH | P2 | PISC | MASJID BAITURRAHMAN 006 | DAIKIN | FWW 1800 | 2.69 | 0.9 |  |  | 0.7 |  |  | 0.2 | 0 | 0 | 17.9 | 17.4 | 0.5 | 22.8 | 22.4 | 0.4 | 5 | 325 | 485 | 160 | 1673.25 | 1800 | 92.96% | NORMAL
408 | 2026-05-28 | BOH | P2 | PISC | MASJID BAITURRAHMAN 007 | DAIKIN | FWW 1800 | 2.69 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 18.7 | 18.3 | 0.4 | 22.8 | 22.5 | 0.3 | 5 | 365 | 481 | 116 | 1659.45 | 1800 | 92.19% | NORMAL
409 | 2026-05-28 | BOH | P2 | PISC | MASJID BAITURRAHMAN 008 | DAIKIN | FWW 1800 | 2.69 | 0.6 |  |  | 0.5 |  |  | 0.1 | 0 | 0 | 17.1 | 16.2 | 0.9 | 22.3 | 21.1 | 1.2 | 5 | 320 | 434 | 114 | 1497.3 | 1800 | 83.18% | NORMAL
410 | 2026-05-28 | BOH | P2 | PISC | MASJID BAITURRAHMAN 009 | DAIKIN | FWW 1800 | 2.69 | 2.48 |  |  | 2.28 |  |  | 0.2 | 0 | 0 | 19.6 | 18.9 | 0.7 | 23.5 | 22.9 | 0.6 | 5 | 312 | 485 | 173 | 1673.25 | 1800 | 92.96% | NORMAL
411 | 2026-05-28 | BOH | P2 | PISC | MASJID BAITURRAHMAN 010 | DAIKIN | FWW 1800 | 2.69 | 2.45 |  |  | 2.38 |  |  | 0.07 | 0 | 0 | 19.4 | 18.1 | 1.3 | 23.2 | 22.8 | 0.4 | 5 | 286 | 468 | 182 | 1614.6 | 1800 | 89.7% | NORMAL
412 | 2026-05-29 | BOH | P2 | PISC | MASJID BAITURRAHMAN 011 | YORK | YCW 1400 | 1,2 | 1.1 |  |  | 1 |  |  | 0.1 | 0 | 0 | 19.5 | 18.9 | 0.6 | 23.1 | 22.7 | 0.4 | 5 | 215 | 330 | 115 | 1138.5 | 1398 | 81.44% | NORMAL
413 | 2026-05-29 | BOH | P2 | PISC | MASJID BAITURRAHMAN 012 | YORK | YCW 1400 | 1,2 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 18.9 | 18.5 | 0.4 | 22.9 | 22.6 | 0.3 | 5 | 331 | 379 | 48 | 1307.55 | 1398 | 93.53% | NORMAL
414 | 2026-05-29 | BOH | P2 | PISC | MASJID BAITURRAHMAN 013 | YORK | YCW 1400 | 1,2 | 0.7 |  |  | 0.6 |  |  | 0.1 | 0 | 0 | 19.8 | 18.4 | 1.4 | 23.5 | 22.7 | 0.8 | 5 | 200 | 345 | 145 | 1190.25 | 1398 | 85.14% | NORMAL
415 | 2026-05-29 | BOH | P2 | PISC | MASJID BAITURRAHMAN 014 | YORK | YCW 1400 | 1,2 | 0.6 |  |  | 0.4 |  |  | 0.2 | 0 | 0 | 18.3 | 17.6 | 0.7 | 22.9 | 22.6 | 0.3 | 5 | 215 | 350 | 135 | 1207.5 | 1398 | 86.37% | NORMAL
416 | 2026-05-01 | BOH | P2 | PISC | LOCKER BM | TRANE | HCCA 14 | 1,8 | 0.9 |  |  | 0.8 |  |  | 0.1 | 0 | 0 | 20.9 | 19.7 | 1.2 | 23.9 | 23.2 | 0.7 | 4 | 300 | 415 | 115 | 1145.4 | 1400 | 81.81% | NORMAL
417 | 2026-05-27 | BOH | P2 | PISC | ESCALATOR TIMUR 001 | MC QUAY | MCC 50 | 2,3 | 1.3 |  |  | 1.2 |  |  | 0.1 | 0 | 0 | 19.5 | 18.2 | 1.3 | 23.4 | 22.1 | 1.3 | 3 | 561 | 677 | 116 | 1401.39 | 1750 | 80.08% | NORMAL
418 | 2026-05-27 | BOH | P2 | PISC | ESCALATOR TIMUR 002 | MC QUAY | MCC 60 | 2.5 | 1.7 |  |  | 1.6 |  |  | 0.1 | 0 | 0 | 19.8 | 18.6 | 1.2 | 23.1 | 22.3 | 0.8 | 3 | 675 | 775 | 100 | 1604.25 | 2000 | 80.21% | NORMAL
419 | 2026-05-29 | BOH | P2 | PISC | CORRIDOR LIFT 3 - 4 | TRANE | HCCA 14 | 1,8 | 1.4 |  |  | 1.2 |  |  | 0.2 | 0 | 0 | 19.3 | 18.6 | 0.7 | 22.9 | 22.5 | 0.4 | 3 | 440 | 524 | 84 | 1084.68 | 1400 | 77.48% | MEDIUM
420 | 2026-05-31 | BOH | P2 | PISC | MUSHOLLAH PRIA N 001 | AICOOL | FC 24 | 0.9 | 0.6 |  |  | 0.4 |  |  | 0.2 | 0 | 0 | 19.7 | 18.7 | 1 | 23.1 | 22 | 1.1 | 3 | 271 | 375 | 104 | 776.25 | 1000 | 77.62% | MEDIUM
421 | 2026-05-31 | BOH | P2 | PISC | MUSHOLLAH PRIA N 002 | AICOOL | FC 24 | 0.9 | 0.5 |  |  | 0.3 |  |  | 0.2 | 0 | 0 | 20.1 | 19 | 1.1 | 24.1 | 23.3 | 0.8 | 3 | 271 | 388 | 117 | 803.16 | 1000 | 80.32% | NORMAL
422 | 2026-05-31 | BOH | P2 | PISC | MUSHOLLAH PRIA N 003 | AICOOL | FC 24 | 0.9 | 0.8 |  |  | 0.6 |  |  | 0.2 | 0 | 0 | 19.4 | 18.8 | 0.6 | 23.5 | 23.1 | 0.4 | 3 | 233 | 390 | 157 | 807.3 | 1000 | 80.73% | NORMAL
423 | 2026-05-31 | BOH | P2 | PISC | MUSHOLLAH PRIA N 004 | AICOOL | FC 24 | 0.9 | 0.4 |  |  | 0.3 |  |  | 0.1 | 0 | 0 | 19.8 | 18.1 | 1.7 | 23.7 | 23 | 0.7 | 3 | 226 | 387 | 161 | 801.09 | 1000 | 80.11% | NORMAL
424 | 2026-05-30 | RETAIL | P2 | PISC | MEISO | MC QUAY | MCC 50 | 2,3 | 1.5 |  |  | 1.4 |  |  | 0.1 | 0 | 0 | 20.3 | 19.9 | 0.4 | 23.5 | 23.3 | 0.2 | 4 | 280 | 450 | 170 | 1242 | 1750 | 70.97% | MEDIUM
425 | 2026-05-29 | BOH | P2 | PISC | ESCALATOR BARAT 001 | TRANE | HCCA 18 | 2.9 | 1.5 |  |  | 1.3 |  |  | 0.2 | 0 | 0 | 18.3 | 17.6 | 0.7 | 22.8 | 22.5 | 0.3 | 3 | 430 | 615 | 185 | 1273.05 | 1800 | 70.72% | MEDIUM
426 | 2026-05-29 | BOH | P2 | PISC | ESCALATOR BARAT 002 | TRANE | HCCA 18 | 2.9 | 1.6 |  |  | 1.4 |  |  | 0.2 | 0 | 0 | 19.2 | 18.5 | 0.7 | 22.9 | 22.6 | 0.3 | 3 | 441 | 630 | 189 | 1304.1 | 1800 | 72.45% | MEDIUM
427 | 2026-05-29 | BOH | P2 | PISC | ESCALATOR GOLD NAILS | MC QUAY | MCC 50 | 2,3 | 1.8 |  |  | 1.7 |  |  | 0.1 | 0 | 0 | 19.6 | 18.5 | 1.1 | 23.7 | 23 | 0.7 | 5 | 335 | 410 | 75 | 1414.5 | 1750 | 80.83% | NORMAL
428 | 2026-05-01 | BOH | P3 | PISC | R. DRIVER TENGAH | TRANE | HFCA 10 | 1,3 | 0.7 |  |  | 0.6 |  |  | 0.1 | 0 | 0 | 21.1 | 20.7 | 0.4 | 23.2 | 22.8 | 0.4 | 3 | 164 | 350 | 186 | 724.5 | 1000 | 72.45% | MEDIUM
429 | 2026-05-29 | BOH | P3 | PISC | ESCALATOR TIMUR | YORK | YSB 54 | 3,70 | 2.9 |  |  | 2.8 |  |  | 0.1 | 0 | 0 | 19.2 | 18.7 | 0.5 | 23.4 | 22.7 | 0.7 | 3 | 640 | 774 | 134 | 1602.18 | 2000 | 80.11% | NORMAL
430 | 2026-05-30 | BOH | P2 | PISC | R. MESIN LIFT 3 - 4 | MC QUAY | MCC 60 | 2,5 | 1.7 |  |  | 1.6 |  |  | 0.1 | 0 | 0 | 19.4 | 18.9 | 0.5 | 23.2 | 22.8 | 0.4 | 4 | 462 | 587 | 125 | 1620.12 | 2000 | 81.01% | NORMAL
431 | 2026-05-30 | BOH | P3 | PISC | CORRIDOR LIFT 15 - 16 | TRANE | HCCA 18 | 2,9 | 2.1 |  |  | 2 |  |  | 0.1 | 0 | 0 | 19.7 | 18.3 | 1.4 | 23.3 | 22.1 | 1.2 | 3 | 576 | 690 | 114 | 1428.3 | 1800 | 79.35% | MEDIUM
432 | 2026-05-31 | BOH | P3 | PISC | MUSHOLLAH WANITA N 001 | AICOOL | FC 24 | 0,9 | 0.4 |  |  | 0.3 |  |  | 0.1 | 0 | 0 | 18.2 | 17.7 | 0.5 | 23.9 | 23 | 0.9 | 3 | 260 | 385 | 125 | 796.95 | 1000 | 79.69% | MEDIUM
433 | 2026-05-31 | BOH | P3 | PISC | MUSHOLLAH WANITA N 002 | AICOOL | FC 24 | 0,9 | 0.2 |  |  | 0.1 |  |  | 0.1 | 0 | 0 | 19.4 | 18.7 | 0.7 | 23.1 | 22.4 | 0.7 | 3 | 230 | 370 | 140 | 765.9 | 1000 | 76.59% | MEDIUM
434 | 2026-05-31 | BOH | P3 | PISC | MUSHOLLAH WANITA N 003 | AICOOL | FC 24 | 0,9 | 0.5 |  |  | 0.4 |  |  | 0.1 | 0 | 0 | 18 | 17.2 | 0.8 | 23.5 | 22.6 | 0.9 | 3 | 220 | 360 | 140 | 745.2 | 1000 | 74.52% | MEDIUM
435 | 2026-05-31 | BOH | P3 | PISC | MUSHOLLAH WANITA N 004 | AICOOL | FC 24 | 0,9 | 0.3 |  |  | 0.2 |  |  | 0.1 | 0 | 0 | 18.2 | 17.4 | 0.8 | 23.5 | 22.3 | 1.2 | 3 | 250 | 375 | 125 | 776.25 | 1000 | 77.62% | MEDIUM
436 | 2026-05-30 | BOH | P3 | PISC | R. STP | YORK | YSB 100 | 8,8 | 7.8 |  |  | 7.65 |  |  | 0.15 | 0 | 0 | 18.3 | 17.5 | 0.8 | 23.2 | 22.6 | 0.6 | 5 | 645 | 785 | 140 | 2708.25 | 3200 | 84.63% | NORMAL
SUMMARY
| SESUAI SCHEDULE |  | 436
| OUT OF SCHEDULE |  | 0
| TOTAL |  | 436
|  |  |  | PT Daikin Applied Solutions Indonesia, |  |  |  |  | Diperiksa oleh, | [10 empty] | Diketahui oleh, | [8 empty] | Disetujui oleh,
|  |  |  | ( Prayogi Prasetyo Nugroho ) |  |  |  |  | ( Ahmad Zani ) | [10 empty] | (Agus Bintoro) | [8 empty] | (Mohammad Riva Noor H)
|  |  |  | O&M Coordinator |  |  |  |  | Spv. BM Operasional & Maintenance | [10 empty] | Operational Retail & Office Section Head | [8 empty] | Operational Facility Manager Retail
Note on F4: ex. TED BAKER 001
Note on F5: ex. TED BAKER 002
Note on F9: ====== ID#AAABtMFu6ls SUCI (2025-10-27 03:25:54) ex. Forest
Note on F10: ====== ID#AAABtMFu6mA SUCI (2025-10-27 03:25:54) ex. Forest
Note on F15: ex. H & M 002
Note on F16: ex. H & M
Note on F17: ex. H & M
Note on F19: ex. H & M 001
Note on F20: ex. H & M 002
Note on F23: ex. LINEA 001
Note on F24: ex. LINEA 002
Note on F36: ====== ID#AAABtMFu6mM SUCI (2025-10-27 03:25:54) ex. L2 KITCHENETTE
Note on F37: ====== ID#AAABtMFu6mw SUCI (2025-10-27 03:25:54) ex. L2 KITCHENETTE
Note on F69: ex. SWAROVSKY
Note on F71: ex. ALDO 001
Note on F72: ex. ALDO 002
Note on F74: ex. MASARI 002
Note on F77: ex. MICHAEL KORS 001
Note on F78: MICHAEL KORS 002
Note on F79: MICHAEL KORS 003
Note on F80: MICHAEL KORS 004
Note on F110: ex. BIKA
Note on F115: ex. ZARA HOME 001
Note on F116: ex. ZARA HOME 002
Note on F117: ex. ZARA HOME 003
Note on F118: ex. ZARA HOME 004
Note on F119: ex. ZARA HOME 005
Note on F128: ex. AIGNER 003
Note on F129: ex. WEEKEND MAXMARA 001
Note on F130: ex. WEEKEND MAXMARA 002
Note on F131: ex. HARLAN + HOLDEN 001
Note on F132: ex. HARLAN + HOLDEN 002
Note on F133: ex. HARLAN + HOLDEN 003
Note on F134: ex. PANDORA
Note on F135: ex. BAHA GIA 001
Note on F136: ex. BAHA GIA 002
Note on F142: EX. HOUSE OF FUTURE 001
Note on F143: ex. HOUSE OF FUTURE 002
Note on F147: ex. H & M 001
Note on F148: ex. H & M 002
Note on F149: ex. H & M 003
Note on F150: ex. H & M 004
Note on F151: ex. H & M 005
Note on F152: ex. H & M 006
Note on F153: ex. H & M 007
Note on F189: ex. ROCKSTAR GYM 001
Note on F190: ex. ROCKSTAR GYM 002
Note on F191: ex. ROCKSTAR GYM 003
Note on F219: ex. OGAWA 001
Note on F220: ex. OGAWA 002
Note on F221: ex. ECOVACS 001
Note on F222: ex. ECOVACS 002
Note on F224: ex. WOMEN'S CO
Note on F225: ex. MAJESTY TOP GOLF
Note on F237: ex. LIFE FITNESS 001
Note on F247: PARIS MIKI
Note on F248: MASSHIRO & CO
Note on F256: ====== ID#AAABtMFu6lY hp (2025-10-27 03:25:54) hp:EX BATIK KERIS
Note on F257: ex. BATIK KERIS 02
Note on F258: ex. BATIK KERIS 03
Note on F259: ====== ID#AAABtMFu6lc hp (2025-10-27 03:25:54) hp: EX KESAWAN
Note on F260: ex. MUSIQUE 001
Note on F261: MUSIQUE 002
Note on F262: ex. MALINDA 001
Note on F263: MALINDA 002
Note on F264: ex. MALINDA 003
Note on F265: ex. BLACKWOOD 001
Note on F266: ex. BLACKWOOD 002
Note on F267: Ex. BLACKWOOD 003
Note on F268: ex. BLACKWOOD 004
Note on F269: ex. BLACKWOOD 005
Note on F270: ex. BLACKWOOD 006
Note on F271: ex. KAM'S ROAST 001
Note on F272: ex. KAM'S ROAST 002
Note on F273: ex. KAM'S ROAST 003
Note on F274: ex. KAM'S ROAST 004
Note on F292: EX. THE GRAND PIANO 001
Note on F293: EX. THE GRAND PIANO 002
Note on F295: ex. NATUZZI ITALY 001
Note on F296: ex. NATUZZI ITALY 002
Note on F297: ex. NATUZZI ITALY 003
Note on F298: ex. NATUZZI ITALY 004
Note on F299: ex. NATUZZI ITALY 005
Note on F300: ex. NATUZZI ITALY 006
Note on F301: ex. NATUZZI ITALY 007
Note on F305: ex. LAZ BOY 001
Note on F306: ex. LAZ BOY 002
Note on F307: CATELLAN ITALIA 001
Note on F308: ====== ID#AAABtMFu6mE hp (2025-10-27 03:25:54) hp:EX CATELLAN 04
Note on F309: ex. HAVANA GALLERY
Note on F315: EICHHOLTZ 001
Note on F316: EICHHOLTZ 002
Note on F317: EICHHOLTZ 003
Note on F318: ex. FRANK & CO 001
Note on F319: ex. FRANK & CO 002
Note on F320: ex. FRANK & CO 003
Note on F323: ex. YANTI JEWELL
Note on F324: ex. PENINSULA JEWELLERY
Note on F325: ex. PASSION PRIVE 001
Note on F326: ex. PASSION PRIVE 002
Note on F327: ex. LIFE FITNESS 001
Note on F330: ex. ELITE 001
Note on F331: ex. ELITE 002
Note on F338: ex. CZARRE 001
Note on F339: ex. CZARRE 002
Note on F341: ex. MUSIQUE / STELLA MCCARTNEY KIDS
Note on F352: ex. J.F LAZARTIGUE 001
Note on F353: ex. J.F LAZARTIGUE 002
Note on F356: ex. LU'VAZE 001
Note on F357: ex. LU'VAZE 002
Note on F358: ex. MELANDAS 001
Note on F359: ex. MELANDAS 002
Note on F365: ex. JOHNY ANDREAN 001
Note on F376: ex. JOHNY ANDREAN 002
Note on F380: ====== ID#AAABtMFu6mk SUCI (2025-10-27 03:25:54) ex. Mad Coco
Note on F388: ex. LIFE HOUSE