## BOQ (Non Cbl Chiler Exis) (1)
BILL OF QUANTITY | [15 empty] | Factor
Proyek |  | : | PT. VISION EASE | [12 empty] | Material | 28%
Pekerjaan |  | : | Renewall Chiller Plant | [12 empty] | Upah | 28%
Tanggal |  | : | 2026-06-25 | [12 empty] | Prelim | 20%
NO | DESCRIPTION | [6 empty] | QTY | SATUAN | UNIT PRICE |  | TOTAL PRICE |  |  |  | UNIT PRICE |  | TOTAL PRICE
[10 empty] | MATERIAL | LABOUR | MATERIAL | LABOUR |  | REFF | MATERIAL | LABOUR | MATERIAL | LABOUR
1 | 2 | [6 empty] | 3 | 4 | 5 | 6 | 7 | 8
I | PRELIMENARY
1 |  | Management Project | [5 empty] | 1 | lot | 0 | 62500000 | 0 | 62500000 |  | Pre-1 | 0 | 50000000 | 0 | 50000000
2 |  | Alat Kerja & Safety | [5 empty] | 1 | lot | 0 | 25000000 | 0 | 25000000 |  | Pre-2 | 0 | 20000000 | 0 | 20000000
3 |  | Test Commmsioning | [5 empty] | 1 | lot | 0 | 9375000 | 0 | 9375000 |  | PRE-13 | 0 | 7500000 | 0 | 7500000 |  | SS3
[21 empty] | HXE | 7725000000
[7 empty] | SUB TOTAL PRELIMENARY |  |  |  |  | 0 | 96875000 |  |  |  |  | 0 | 77500000
II | SUPPLY MAIN EQUIPMENT
Supply Main Equipment
1 | Water Cooled Chiller | [6 empty] | 3 | unit | 4000000000 | 18750000 | 12000000000 | 56250000 |  |  |  | 15000000 | 0 | 45000000
|  | Model |  | : | Single Screw Water Cooled Chiller
|  | Type |  | : | HTS100MAZ59F/E3012-PH-2/C3012-EK-2
|  | Evap Waterflow |  | : | 820 | Gpm
[5 empty] | 186.3636 | m3/hr
|  | Cond Waterflow |  | : | 960.2 | Gpm
[5 empty] | 218.2273 | m3/hr
|  | Power input |  | : | 173.2 | kW
|  | Cooling Capacity |  | : | 600 | TR
|  | Evap Connection Pipe |  | :
|  | Evap Inlet |  | : | 8 | inch
|  | Evap Outlet |  | : | 8 | inch
|  | Cond Connection Pipe |  | :
|  | Cond Inlet |  | : | 8 | Inch
|  | Cond Outlet |  | : | 8 | Inch
|  | Evap EWT/LWT |  | : | 11/6 | °C
|  | Cond EWT/LWT |  | : | 30/35 | °C
|  | Power Source |  | : | 380/3N/50Hz
|  | Starter Type |  | : | Y-Delta
|  | Dimension (L x W x H) |  | : | 4420mm x1821mm x 2336 mm
|  | Operation Weight |  | : | 7260 Kg
2 | Cooling Tower | [6 empty] | 3 | unit | 613426000 | 18750000 | 1840278000 | 56250000 |  |  | 441666667 | 15000000 | 1325000001 | 45000000
|  | Model |  | : | 65-SKB-450R
|  | Type |  | : | Open-Circuit Cooling Tower
|  | Power input |  | : | 18.5 | kW
|  | Power Source |  | : | 380/3N/50Hz
|  | Ambient Temp. |  | : | 27 | °C WB
|  | Entering Water Temp. |  | : | 35 | °C
|  | Leaving Water Temp. |  | : | 30 | °C
|  | Water Flow Rate |  | : | 3634.4 | L/min | 218.064
[5 empty] | 219 | m3/hr
|  | Connection Pipe |  | :
|  | Water Inlet |  | : | 5 | Inch | x 2
|  | Water Outlet |  | : | 5 | Inch | x 2
|  | Overflow |  | : | 2 | Inch | x 2
|  | Drain |  | : | 1.25 | Inch
|  | Make Up Water |  | : | 1.25 | Inch | Include Floating Valve
|  | Equalizer |  | : | 5 | Inch
|  | Dimension (L x W x H) |  | : | 3530mm x 4500mm x 2630mm
|  | Operation Weight |  | : | 6120 Kg
|  | Type |  | : | Open-Circuit Cooling Tower
|  | Ambient Temp. |  | : | 27 | °C WB
|  | Entering Water Temp. |  | : | 35 | °C
|  | Leaving Water Temp. |  | : | 30 | °C
|  | Water Flow Rate |  | : | 468 | m3/hr
|  | Connection Pipe |  | :
|  | Water Inlet |  | : | 8 | Inch | x 2
|  | Water Outlet |  | : | 12 | Inch
|  | Overflow |  | : | 4 | Inch
|  | Drain |  | : | 2 | Inch
|  | Make Up Water |  | : | 2 | Inch | Include Floating Valve
|  | Equalizer |  | : | 5 | Inch
|  | Dimension (L x W x H) |  | : | 4070 mm x 6930 mm x 5970 mm
|  | Operation Weight |  | : | 12890 Kg
3 | Primary Chilled Water Pump for Chiller | [6 empty] | 3 | unit | 126862500 | 9375000 | 380587500 | 28125000 |  |  | 101490000 | 7500000 | 304470000 | 22500000
|  | Tag Number |  | : | CWP-1-1-3
|  | Model Pump |  | : | 300 x 250 CNFA 5 55
|  | Type |  | : | Horizontal Split Casing
|  | Entering Temp |  | : | 6°C
|  | Flow Rate |  | : | 12420 l/min
|  | Head |  | : | 20 m
|  | Connection Pipe |  | :
|  |  | Size Suction Pipe | : | 12 inch
|  |  | Size Discharge Pipe | : | 10 inch
|  | Power |  | : | 55 kW
|  | Speed |  | : | 1450 rpm
|  | Power Source |  | : | 380/3N/50Hz
|  | Remarks |  | : | 2 Running 1 Stand By
4 | Secondary Chilled Water Pump | [6 empty] | 1 | unit | 680200000 | 9375000 | 680200000 | 9375000 |  |  | 544160000 | 7500000 | 544160000 | 7500000
|  | Tag Number |  | : | CWP-2-1-3
|  | Type |  | : | End Suction Volute Pump
|  | Entering Temp |  | : | 6 °C
|  | Flow Rate |  | : | 12422 l/min
|  | Head |  | : | 35 m
|  | Connection Pipe |  | :
|  |  | Size Suction Pipe | : | 10 inch
|  |  | Size Discharge Pipe | : | 8 inch
|  | Power |  | : | 110 kW
|  | Power Source |  | : | 380/3N/50Hz
|  | Remarks |  | : | 2 Running 1 Stand By
5 | Condenser Water Pump for Chiller | [6 empty] | 3 | unit | 195062500 | 9375000 | 585187500 | 28125000 |  |  | 156050000 | 7500000 | 468150000 | 22500000
|  | Tag Number |  | : | CDP-1-2
|  | Type |  | : | End Suction Volute Pump
|  | Entering Temp |  | : | 30°C
|  | Flow Rate |  | : | 14537.6 l/min
|  | Head |  | : | 20 m
|  | Connection Pipe |  | :
|  |  | Size Suction Pipe | : | 10 inch
|  |  | Size Discharge Pipe | : | 8 inch
|  | Remarks |  | : | 1 Running 1 Stand By
|  | Power |  | : | 90 kW
|  | Power Source |  | : | 380/3N/50Hz
6 | Expansion water Tank | [6 empty] | 1 | unit | 55555600 | 17500000 | 55555600 | 17500000 |  |  | 40000000 | 14000000 | 40000000 | 14000000
|  | Type |  | : | Expansion water Tank
|  | Volume |  | : | 1000 | Liter
|  | Material |  | : | Stainless Steel
|  | Insulation |  | : | ArmaFlex 50mm + Almunium Sheet 0.6 mm
|  | Make Up Water |  | : | 0.75 | Inch | Include Floating Valve
7 | Panel Power & Power Control | [6 empty] | 1 | unit | 2083333400 | 28125000 | 2083333400 | 28125000 |  |  | 1500000000 | 22500000 | 1500000000 | 22500000
|  | Type/Model |  | : | Outdoor Floor Standing
|  | Power |  | : | 1520 | kW
|  | Power Source |  | : | 380 V /3N/50 Hz
[7 empty] | SUB TOTAL MAIN EQUIPMENT |  |  |  |  | 17625142000 | 223750000 |  |  |  |  | 4181780001 | 179000000
III | SCOPE OF WORK INSTALLATION
Working for supply and Installation Pipe, Electrical, Insulation, Jacketing
A | INSTALLATION PIPE
1 | PIPE CHILLER WATER SUPPLY
| - | Pipe Blacksteel Sch 40 size |  | : | 18 inch |  |  | 120 | m' | 5791700 | 2027100 | 695004000 | 243252000 |  | BS.ISO.SCH40.8 | 4170000 | 1459500 | 500400000 | 175140000
| - | Pipe Blacksteel Sch 40 size |  | : | 14 inch |  |  | 40 | m' | 4997300 | 1749100 | 199892000 | 69964000 |  | BS.ISO.SCH40.8 | 3598000 | 1259300 | 143920000 | 50372000
| - | Pipe Blacksteel Sch 40 size |  | : | 10 inch |  |  | 18 | m' | 2895900 | 1013600 | 52126200 | 18244800 |  | BS.ISO.SCH40.8 | 2085000 | 729750 | 37530000 | 13135500
| - | Pipe Blacksteel Sch 40 size |  | : | 8 inch |  |  | 58 | m' | 2498700 | 874600 | 144924600 | 50726800 |  | BS.ISO.SCH40.8 | 1799000 | 629650 | 104342000 | 36519700
| - | Pipe Blacksteel Sch 40 size |  | : | 2 inch |  |  | 25 | m' | 341700 | 119600 | 8542500 | 2990000 |  | BS.ISO.SCH40.8 | 246000 | 86100 | 6150000 | 2152500
| - | Tee Weld Blacksteel Sch 40 size |  | : | 18 x 18 inch |  |  | 12 | pcs | 5494500 | 1923100 | 65934000 | 23077200 |  | BS.ISO.SCH40.8 | 3956000 | 1384600 | 47472000 | 16615200
| - | Tee Weld Blacksteel Sch 40 size |  | : | 14x 14 inch |  |  | 2 | pcs | 6190300 | 2166600 | 12380600 | 4333200 |  | BS.ISO.SCH40.8 | 4457000 | 1559950 | 8914000 | 3119900
| - | Tee Screw Blacksteel Sch 40 size |  | : | 1/2 inch |  |  | 4 | pcs | 114300 | 40000 | 457200 | 160000 |  | BS.ISO.SCH40.8 | 82260 | 28791 | 329040 | 115164
| - | Reducer Weld Blacksteel Sch 40 size |  | : | 18 x 14 inch |  |  | 2 | pcs | 7450000 | 2607500 | 14900000 | 5215000 |  | BS.ISO.SCH40.8 | 5364000 | 1877400 | 10728000 | 3754800
| - | Reducer Weld Blacksteel Sch 40 size |  | : | 18 x 8 inch |  |  | 12 | pcs | 6112500 | 2139400 | 73350000 | 25672800 |  | BS.ISO.SCH40.8 | 4401000 | 1540350 | 52812000 | 18484200
| - | Reducer Weld Blacksteel Sch 40 size |  | : | 14 x 10 inch |  |  | 1 | pcs | 3004500 | 1051600 | 3004500 | 1051600 |  | BS.ISO.SCH40.8 | 2163200 | 757120 | 2163200 | 757120
| - | Reducer Weld Blacksteel Sch 40 size |  | : | 14 x 8 inch |  |  | 3 | pcs | 3821900 | 1337700 | 11465700 | 4013100 |  | BS.ISO.SCH40.8 | 2751700 | 963095 | 8255100 | 2889285
| - | Reducer Weld Blacksteel Sch 40 size |  | : | 10 x 8 inch |  |  | 3 | pcs | 1684800 | 589700 | 5054400 | 1769100 |  | BS.ISO.SCH40.8 | 1213000 | 424550 | 3639000 | 1273650
| - | Reducer Weld Blacksteel Sch 40 size |  | : | 10 x 5 inch |  |  | 3 | pcs | 913500 | 319800 | 2740500 | 959400 |  | BS.ISO.SCH40.8 | 657700 | 230195 | 1973100 | 690585
| - | Reducer Weld Blacksteel Sch 40 size |  | : | 8 x 6 inch |  |  | 3 | pcs | 1130700 | 395800 | 3392100 | 1187400 |  | BS.ISO.SCH40.8 | 814100 | 284935 | 2442300 | 854805
| - | Elbow Weld Blacksteel Sch 40 size |  | : | 18 inch |  |  | 10 | pcs | 8902800 | 3116000 | 89028000 | 31160000 |  | BS.ISO.SCH40.8 | 6410000 | 2243500 | 64100000 | 22435000
| - | Elbow Weld Blacksteel Sch 40 size |  | : | 14 inch |  |  | 10 | pcs | 5404200 | 1891500 | 54042000 | 18915000 |  | BS.ISO.SCH40.8 | 3891000 | 1361850 | 38910000 | 13618500
| - | Elbow Weld Blacksteel Sch 40 size |  | : | 10 inch |  |  | 8 | pcs | 3600000 | 1260000 | 28800000 | 10080000 |  | BS.ISO.SCH40.8 | 2592000 | 907200 | 20736000 | 7257600
| - | Elbow Weld Blacksteel Sch 40 size |  | : | 8 inch |  |  | 14 | pcs | 2404200 | 841500 | 33658800 | 11781000 |  | BS.ISO.SCH40.8 | 1731000 | 605850 | 24234000 | 8481900
| - | Elbow Weld Blacksteel Sch 40 size |  | : | 2 inch |  |  | 4 | pcs | 79200 | 27800 | 316800 | 111200 |  | BS.ISO.SCH40.8 | 57000 | 19950 | 228000 | 79800
| - | Elbow Screw Blacksteel Sch 40 size |  | : | 1/2 inch |  |  | 2 | pcs | 231500 | 81000 | 463000 | 162000 |  | BS.ISO.SCH40.8 | 166620 | 58317 | 333240 | 116634
| - | Flange Blacksteel JIS 10K size |  | : | 18 inch |  |  | 6 | pcs | 1793100 | 627600 | 10758600 | 3765600 |  | BS.ISO.SCH40.8 | 1291000 | 451850 | 7746000 | 2711100
| - | Flange Blacksteel JIS 10K size |  | : | 14 inch |  |  | 14 | pcs | 1105600 | 387000 | 15478400 | 5418000 |  | BS.ISO.SCH40.8 | 796000 | 278600 | 11144000 | 3900400
| - | Flange Blacksteel JIS 10K size |  | : | 12 inch |  |  | 8 | pcs | 805600 | 282000 | 6444800 | 2256000 |  | BS.ISO.SCH40.8 | 580000 | 203000 | 4640000 | 1624000
| - | Flange Blacksteel JIS 10K size |  | : | 10 inch |  |  | 12 | pcs | 779200 | 272800 | 9350400 | 3273600 |  | BS.ISO.SCH40.8 | 561000 | 196350 | 6732000 | 2356200
| - | Flange Blacksteel JIS 10K size |  | : | 8 inch |  |  | 42 | pcs | 516700 | 180900 | 21701400 | 7597800 |  | BS.ISO.SCH40.8 | 372000 | 130200 | 15624000 | 5468400
| - | Flange Blacksteel PN 16 size |  | : | 8 inch |  |  | 8 | pcs | 516700 | 180900 | 4133600 | 1447200 |  | BS.ISO.SCH40.8 | 372000 | 130200 | 2976000 | 1041600
| - | Blind Flange Blacksteel JIS 10K size |  | : | 18 inch |  |  | 5 | pcs | 4286200 | 1500200 | 21431000 | 7501000 |  | BS.ISO.SCH40.8 | 3086000 | 1080100 | 15430000 | 5400500
| - | Shock Weld Blacksteel size |  | : | 3/4 inch |  |  | 2 | pcs | 94700 | 33200 | 189400 | 66400 |  | BS.ISO.SCH40.8 | 68160 | 23856 | 136320 | 47712
| - | Shock Weld Blacksteel size |  | : | 1/2 inch |  |  | 23 | pcs | 70000 | 24500 | 1610000 | 563500 |  | BS.ISO.SCH40.8 | 50340 | 17619 | 1157820 | 405237
| - | D-Nipple Blacksteel size |  | : | 3/4 inch |  |  | 13 | pcs | 39500 | 13900 | 513500 | 180700 |  | BS.ISO.SCH40.8 | 28440 | 9954 | 369720 | 129402
| - | D-Nipple Blacksteel size |  | : | 1/2 inch |  |  | 19 | pcs | 29500 | 10300 | 560500 | 195700 |  | BS.ISO.SCH40.8 | 21180 | 7413 | 402420 | 140847
2 | PIPE CONDENSER WATER SUPPLY
| - | Pipe Galvanize Medium size |  | : | 20 inch |  |  | 85 | m' | 7076100 | 2476700 | 601468500 | 210519500 |  | BS.ISO.SCH40.8 | 5094750 | 1783162.5 | 433053750 | 151568812.5
| - | Pipe Galvanize Medium size |  | : | 16 inch |  |  | 60 | m' | 2567400 | 898600 | 154044000 | 53916000 |  | BS.ISO.SCH40.8 | 1848500 | 646975 | 110910000 | 38818500
| - | Pipe Galvanize Medium size |  | : | 12 inch |  |  | 6 | m' | 2037300 | 713100 | 12223800 | 4278600 |  | BS.ISO.SCH40.8 | 1466833.3333 | 513391.6667 | 8801000 | 3080350
| - | Pipe Galvanize Medium size |  | : | 10 inch |  |  | 65 | m' | 1711900 | 599200 | 111273500 | 38948000 |  | BS.ISO.SCH40.8 | 1232500 | 431375 | 80112500 | 28039375
| - | Pipe Galvanize Medium size |  | : | 8 inch |  |  | 45 | m' | 1934100 | 677000 | 87034500 | 30465000 |  | BS.ISO.SCH40.8 | 1392500 | 487375 | 62662500 | 21931875
| - | Pipe Galvanize Medium size |  | : | 3 inch |  |  | 6 | m' | 471300 | 165000 | 2827800 | 990000 |  | BS.ISO.SCH40.8 | 339333.3333 | 118766.6667 | 2036000 | 712600
| - | Pipe Galvanize Medium size |  | : | 2 1/2 inch |  |  | 18 | m' | 364900 | 127700 | 6568200 | 2298600 |  | BS.ISO.SCH40.8 | 262666.6667 | 91933.3333 | 4728000 | 1654800
| - | Pipe Galvanize Medium size |  | : | 2 inch |  |  | 18 | m' | 329100 | 115200 | 5923800 | 2073600 |  | BS.ISO.SCH40.8 | 236900 | 82915 | 4264200 | 1492470
| - | Pipe PVC Class AW size |  | : | 2 inch |  |  | 30 | m' | 98300 | 34400 | 2949000 | 1032000 |  | BS.ISO.SCH40.8 | 70750 | 24762.5 | 2122500 | 742875
| - | Pipe Galvanize Medium size |  | : | 1 1/4 inch |  |  | 24 | m' | 210000 | 73500 | 5040000 | 1764000 |  | BS.ISO.SCH40.8 | 151129.1667 | 52895.2083 | 3627100 | 1269485
| - | Pipe Galvanize Medium size |  | : | 3/4 inch |  |  | 18 | m' | 158600 | 55500 | 2854800 | 999000 |  | BS.ISO.SCH40.8 | 114137.5 | 39948.125 | 2054475 | 719066.25
| - | Tee Weld Galvanize size |  | : | 20 x 16 inch |  |  | 1 | pcs | 11180600 | 3913200 | 11180600 | 3913200 |  | BS.ISO.SCH40.8 | 8050000 | 2817500 | 8050000 | 2817500
| - | Tee Weld Galvanize size |  | : | 20 x 12 inch |  |  | 3 | pcs | 12218800 | 4276600 | 36656400 | 12829800 |  | BS.ISO.SCH40.8 | 8797500 | 3079125 | 26392500 | 9237375
| - | Tee Weld Galvanize size |  | : | 20 x 10 inch |  |  | 15 | pcs | 13304900 | 4656800 | 199573500 | 69852000 |  | BS.ISO.SCH40.8 | 9579500 | 3352825 | 143692500 | 50292375
| - | Tee Weld Galvanize size |  | : | 16 x 10 inch |  |  | 3 | pcs | 13547800 | 4741800 | 40643400 | 14225400 |  | BS.ISO.SCH40.8 | 9754400 | 3414040 | 29263200 | 10242120
| - | Tee Weld Galvanize size |  | : | 10 x 10 Inch |  |  | 3 | pcs | 4840300 | 1694100 | 14520900 | 5082300 |  | BS.ISO.SCH40.8 | 3485000 | 1219750 | 10455000 | 3659250
| - | Tee Weld Galvanize size |  | : | 3 x 2 inch |  |  | 3 | pcs | 372500 | 130400 | 1117500 | 391200 |  | BS.ISO.SCH40.8 | 268200 | 93870 | 804600 | 281610
| - | Tee Screw Galvanize size |  | : | 3 x 1 inch |  |  | 1 | pcs | 372500 | 130400 | 372500 | 130400 |  | BS.ISO.SCH40.8 | 268200 | 93870 | 268200 | 93870
| - | Tee Screw Galvanize size |  | : | 3/4 x 3/4 inch |  |  | 1 | pcs | 50000 | 17500 | 50000 | 17500 |  | BS.ISO.SCH40.8 | 36000 | 12600 | 36000 | 12600
| - | Tee PVC Class AW size |  | : | 2 x 2 inch |  |  | 20 | pcs | 45900 | 16100 | 918000 | 322000 |  | BS.ISO.SCH40.8 | 33000 | 11550 | 660000 | 231000
| - | Reducer Weld Galvanize size |  | : | 20 x 16 inch |  |  | 5 | pcs | 11459100 | 4010700 | 57295500 | 20053500 |  | BS.ISO.SCH40.8 | 8250500 | 2887675 | 41252500 | 14438375
| - | Reducer Weld Galvanize size |  | : | 10 x 8 inch |  |  | 9 | pcs | 1603200 | 561200 | 14428800 | 5050800 |  | BS.ISO.SCH40.8 | 1154300 | 404005 | 10388700 | 3636045
| - | Reducer Weld Galvanize size |  | : | 10 x 6 inch |  |  | 3 | pcs | 1329400 | 465300 | 3988200 | 1395900 |  | BS.ISO.SCH40.8 | 957100 | 334985 | 2871300 | 1004955
| - | Reducer Screw Galvanize size |  | : | 1 x 3/4 inch |  |  | 1 | pcs | 36200 | 12700 | 36200 | 12700 |  | BS.ISO.SCH40.8 | 26000 | 9100 | 26000 | 9100
| - | Elbow Weld Galvanize size |  | : | 20 inch |  |  | 4 | pcs | 9909800 | 3468500 | 39639200 | 13874000 |  | BS.ISO.SCH40.8 | 7135000 | 2497250 | 28540000 | 9989000
| - | Elbow Weld Galvanize size |  | : | 16 inch |  |  | 4 | pcs | 5394500 | 1888100 | 21578000 | 7552400 |  | BS.ISO.SCH40.8 | 3884000 | 1359400 | 15536000 | 5437600
| - | Elbow Weld Galvanize size |  | : | 12 inch |  |  | 4 | pcs | 5016700 | 1755900 | 20066800 | 7023600 |  | BS.ISO.SCH40.8 | 3612000 | 1264200 | 14448000 | 5056800
| - | Elbow Weld Galvanize size |  | : | 10 inch |  |  | 23 | pcs | 2913900 | 1019900 | 67019700 | 23457700 |  | BS.ISO.SCH40.8 | 2098000 | 734300 | 48254000 | 16888900
| - | Elbow Weld Galvanize size |  | : | 8 inch |  |  | 12 | pcs | 2404200 | 841500 | 28850400 | 10098000 |  | BS.ISO.SCH40.8 | 1731000 | 605850 | 20772000 | 7270200
| - | Elbow Screw Galvanize size |  | : | 3/4 inch |  |  | 3 | pcs | 20900 | 7300 | 62700 | 21900 |  | BS.ISO.SCH40.8 | 15000 | 5250 | 45000 | 15750
| - | Elbow PVC Class AW size |  | : | 2 inch |  |  | 20 | pcs | 32000 | 11200 | 640000 | 224000 |  | BS.ISO.SCH40.8 | 23000 | 8050 | 460000 | 161000
| - | Flange Galvanize JIS 10K size |  | : | 20 inch |  |  | 7 | pcs | 2077800 | 727300 | 14544600 | 5091100 |  | BS.ISO.SCH40.8 | 1496000 | 523600 | 10472000 | 3665200
| - | Flange Galvanize JIS 10K size |  | : | 16 inch |  |  | 2 | pcs | 1402800 | 491000 | 2805600 | 982000 |  | BS.ISO.SCH40.8 | 1010000 | 353500 | 2020000 | 707000
| - | Flange Galvanize JIS 10K size |  | : | 12 inch |  |  | 6 | pcs | 805600 | 282000 | 4833600 | 1692000 |  | BS.ISO.SCH40.8 | 580000 | 203000 | 3480000 | 1218000
| - | Flange Galvanize JIS 10K size |  | : | 10 inch |  |  | 36 | pcs | 779200 | 272800 | 28051200 | 9820800 |  | BS.ISO.SCH40.8 | 561000 | 196350 | 20196000 | 7068600
| - | Flange Galvanize PN16 size |  | : | 10 inch |  |  | 24 | pcs | 1168800 | 409100 | 28051200 | 9818400 |  | BS.ISO.SCH40.8 | 841500 | 294525 | 20196000 | 7068600
| - | Flange Galvanize JIS 10K size |  | : | 8 inch |  |  | 12 | pcs | 516700 | 180900 | 6200400 | 2170800 |  | BS.ISO.SCH40.8 | 372000 | 130200 | 4464000 | 1562400
| - | Flange Galvanize JIS 10K size |  | : | 2.5 inch |  |  | 1 | pcs | 162500 | 56900 | 162500 | 56900 |  | BS.ISO.SCH40.8 | 117000 | 40950 | 117000 | 40950
| - | Flange Galvanize JIS 10K size |  | : | 2 inch |  |  | 14 | pcs | 130600 | 45700 | 1828400 | 639800 |  | BS.ISO.SCH40.8 | 94000 | 32900 | 1316000 | 460600
| - | Blind Flange Galvanize JIS 10K size |  | : | 20 inch |  |  | 7 | pcs | 5666700 | 1983400 | 39666900 | 13883800 |  | BS.ISO.SCH40.8 | 4080000 | 1428000 | 28560000 | 9996000
| - | Blind Flange Galvanize JIS 10K size |  | : | 16 inch |  |  | 2 | pcs | 3187500 | 1115700 | 6375000 | 2231400 |  | BS.ISO.SCH40.8 | 2295000 | 803250 | 4590000 | 1606500
| - | Shock Drat Luar PVC Class AW size |  | : | 2 inch |  |  | 24 | pcs | 44500 | 15600 | 1068000 | 374400 |  | BS.ISO.SCH40.8 | 32000 | 11200 | 768000 | 268800
| - | Shock Weld Galvanize size |  | : | 3/4 inch |  |  | 2 | pcs | 67100 | 23500 | 134200 | 47000 |  | BS.ISO.SCH40.8 | 48260 | 16891 | 96520 | 33782
| - | Shock Weld Galvanize size |  | : | 1/2 inch |  |  | 35 | pcs | 49500 | 17400 | 1732500 | 609000 |  | BS.ISO.SCH40.8 | 35640 | 12474 | 1247400 | 436590
| - | D-Nipple Blacksteel size |  | : | 1/2 inch |  |  | 25 | pcs | 29500 | 10300 | 737500 | 257500 |  | BS.ISO.SCH40.8 | 21180 | 7413 | 529500 | 185325
2 | Accessories Chiller
| - | Butterfly Valve Handle Gear |  | : | 10 | Inch | Brand : Kitz | 6 | pcs | 12500000 | 4375000 | 75000000 | 26250000 |  |  | 9000000 | 3150000 | 54000000 | 18900000
|  |  |  | : | 8 | Inch | Brand : Kitz | 8 | pcs | 8712500 | 3049400 | 69700000 | 24395200 |  |  | 6273000 | 2195550 | 50184000 | 17564400
| - | Butterfly Motorized Valve [On/Off] |  | : | 10 | Inch | Brand : Honeywell | 0 | pcs | 63993900 | 22397900 | 0 | 0 |  |  | 46075578 | 16126452.3 | 0 | 0
|  |  |  | : | 8 | Inch | Brand : Honeywell | 0 | pcs | 47476200 | 16616700 | 0 | 0 |  |  | 34182838.05 | 11963993.3175 | 0 | 0
| - | Flexible Rubber [O-Flex] |  | : | 10 | Inch | Brand : Tozen | 6 | pcs | 14658400 | 5130500 | 87950400 | 30783000 |  |  | 10554000 | 3693900 | 63324000 | 22163400
|  |  |  | : | 8 | Inch | Brand : Tozen | 6 | pcs | 9698700 | 3394600 | 58192200 | 20367600 |  |  | 6983000 | 2444050 | 41898000 | 14664300
| - | Pressure Gauge [ 0 - 10 kgf/cm²] |  | : | 4 | Inch | Brand : Wika include Glyserin | 12 | pcs | 1440300 | 504100 | 17283600 | 6049200 |  |  | 1037000 | 362950 | 12444000 | 4355400
| - | Thermometer [ 0 - 50°C ] |  | : |  |  | Brand : Sika | 12 | pcs | 1754200 | 614000 | 21050400 | 7368000 |  |  | 1263000 | 442050 | 15156000 | 5304600
| - | Gate Valve |  | : | 1/2 | Inch | Brand : Kitz | 14 | pcs | 536200 | 187700 | 7506800 | 2627800 |  |  | 386000 | 135100 | 5404000 | 1891400
| - | Automatic Airvent |  | : | 1/2 | Inch | Brand : Kitz | 2 | pcs | 7372300 | 2580300 | 14744600 | 5160600 |  |  | 5308000 | 1857800 | 10616000 | 3715600
3 | Accessories Primary Chiller Water Pump
| - | Butterfly Valve Handle Gear |  | : | 8 | Inch | Brand : Kitz | 6 | pcs | 8712500 | 3049400 | 52275000 | 18296400 |  |  | 6273000 | 2195550 | 37638000 | 13173300
| - | Flexible Rubber [O-Flex] |  | : | 8 | Inch | Brand : Tozen | 6 | pcs | 9698700 | 3394600 | 58192200 | 20367600 |  |  | 6983000 | 2444050 | 41898000 | 14664300
| - | Strainer |  | : | 8 | Inch | Brand : Kitz | 3 | pcs | 42218100 | 14776400 | 126654300 | 44329200 |  |  | 30397000 | 10638950 | 91191000 | 31916850
| - | Check Valve |  | : | 8 | Inch | Brand : Kitz | 3 | pcs | 64911200 | 22718900 | 194733600 | 68156700 |  |  | 46736000 | 16357600 | 140208000 | 49072800
| - | Pressure Gauge [ 0 - 10 kgf/cm²] |  | : | 4 | Inch | Brand : Wika include Glyserin | 3 | pcs | 1440300 | 504100 | 4320900 | 1512300 |  |  | 1037000 | 362950 | 3111000 | 1088850
| - | Gate Valve |  | : | 1/2 | Inch | Brand : Kitz | 6 | pcs | 536200 | 187700 | 3217200 | 1126200 |  |  | 386000 | 135100 | 2316000 | 810600
| - | Automatic Airvent |  | : | 1/2 | Inch | Brand : Kitz | 1 | pcs | 7372300 | 2580300 | 7372300 | 2580300 |  |  | 5308000 | 1857800 | 5308000 | 1857800
0
4 | Accessories Secondary Chiller Water Pump | [15 empty] | 0
| - | Butterfly Valve Handle Gear |  | : | 14 | Inch | Brand : Kitz | 2 | pcs | 23829200 | 8340300 | 47658400 | 16680600 |  |  | 17157000 | 6004950 | 34314000 | 12009900
| - | Flexible Rubber [O-Flex] |  | : | 14 | Inch | Brand : Tozen | 2 | pcs | 27448700 | 9607100 | 54897400 | 19214200 |  |  | 19763000 | 6917050 | 39526000 | 13834100
| - | Strainer |  | : | 14 | Inch | Brand : Kitz | 1 | pcs | 276272300 | 96695300 | 276272300 | 96695300 |  |  | 198916000 | 69620600 | 198916000 | 69620600
| - | Check Valve |  | : | 14 | Inch | Brand : Kitz | 1 | pcs | 190868100 | 66803900 | 190868100 | 66803900 |  |  | 137425000 | 48098750 | 137425000 | 48098750
| - | Pressure Gauge [ 0 - 16 kgf/cm²] |  | : | 4 | Inch | Brand : Wika include Glyserin | 2 | pcs | 1440300 | 504100 | 2880600 | 1008200 |  |  | 1037000 | 362950 | 2074000 | 725900
| - | Gate Valve |  | : | 1/2 | Inch | Brand : Kitz | 2 | pcs | 536200 | 187700 | 1072400 | 375400 |  |  | 386000 | 135100 | 772000 | 270200
| - | Automatic Airvent |  | : | 1/2 | Inch | Brand : Kitz | 1 | pcs | 7372300 | 2580300 | 7372300 | 2580300 |  |  | 5308000 | 1857800 | 5308000 | 1857800
5 | Accessories Condenser Water Pump
| - | Butterfly Valve Handle Gear |  | : | 10 | Inch | Brand : Kitz | 6 | pcs | 12500000 | 4375000 | 75000000 | 26250000 |  |  | 9000000 | 3150000 | 54000000 | 18900000
| - | Flexible Rubber [O-Flex] |  | : | 10 | Inch | Brand : Tozen | 6 | pcs | 14658400 | 5130500 | 87950400 | 30783000 |  |  | 10554000 | 3693900 | 63324000 | 22163400
| - | Strainer |  | : | 10 | Inch | Brand : Kitz | 3 | pcs | 72575000 | 25401300 | 217725000 | 76203900 |  |  | 52254000 | 18288900 | 156762000 | 54866700
| - | Check Valve |  | : | 12 | Inch | Brand : Kitz | 3 | pcs | 101655600 | 35579500 | 304966800 | 106738500 |  |  | 73192000 | 25617200 | 219576000 | 76851600
| - | Pressure Gauge [ 0 - 10 kgf/cm²] |  | : | 4 | Inch | Brand : Wika include Glyserin | 6 | pcs | 1440300 | 504100 | 8641800 | 3024600 |  |  | 1037000 | 362950 | 6222000 | 2177700
| - | Gate Valve |  | : | 1/2 | Inch | Brand : Kitz | 12 | pcs | 536200 | 187700 | 6434400 | 2252400 |  |  | 386000 | 135100 | 4632000 | 1621200
| - | Automatic Airvent |  | : | 1/2 | Inch | Brand : Kitz | 1 | pcs | 7372300 | 2580300 | 7372300 | 2580300 |  |  | 5308000 | 1857800 | 5308000 | 1857800
6 | Accessories Cooling Tower
` | - | Butterfly Motorized Valve [On/Off] |  | : | 10 | Inch | Brand : Honeywell | 0 | pcs | 63993900 | 22397900 | 0 | 0 |  |  | 46075578 | 16126452.3 | 0 | 0
| - | Butterfly Valve Handle Gear |  | : | 12 | Inch | Brand : Kitz | 3 | pcs | 21866700 | 7653400 | 65600100 | 22960200 |  |  | 15744000 | 5510400 | 47232000 | 16531200
|  |  |  | : | 10 | Inch | Brand : Kitz | 3 | pcs | 8712500 | 3049400 | 26137500 | 9148200 |  |  | 6273000 | 2195550 | 18819000 | 6586650
|  |  |  | : | 8 | Inch | Brand : Kitz | 6 | pcs | 8712500 | 3049400 | 52275000 | 18296400 |  |  | 6273000 | 2195550 | 37638000 | 13173300
| - | Gate Valve |  | : | 2 | Inch | Brand : Kitz | 10 | pcs | 1962500 | 686900 | 19625000 | 6869000 |  |  | 1413000 | 494550 | 14130000 | 4945500
|  |  |  | : | 0.75 | Inch | Brand : Kitz | 2 | pcs | 536200 | 187700 | 1072400 | 375400 |  |  | 386000 | 135100 | 772000 | 270200
| - | Check Valve |  | : | 3/4 | Inch | Brand : Kitz | 1 | pcs | 1091700 | 382100 | 1091700 | 382100 |  |  | 786000 | 275100 | 786000 | 275100
| - | Ball Valve |  | : | 3/4 | Inch | Brand : Kitz | 2 | pcs | 870900 | 304800 | 1741800 | 609600 |  |  | 627000 | 219450 | 1254000 | 438900
[7 empty] | SUB TOTAL INSTALLATION PIPE |  |  |  |  | 5533535500 | 1936780200 |  |  |  |  | 3984095205 | 1394433321.75
B | INSTALLATION ELECTRICAL
Cable Power Incoming New Panel Operationa By Owner
1 | Sensor & Controling
| - | Pressure Sensor |  | : | PTG60B-G5C1AG4-M-1H [Azbil] |  |  | 1 | pcs | 33472300 | 11715300 | 33472300 | 11715300 |  |  | 24100000 | 8435000 | 24100000 | 8435000
| - | Pressure Controller |  | : | SDC35TCOUA2400 [Azbil] |  |  | 1 | pcs | 9861200 | 3451400 | 9861200 | 3451400 |  |  | 7100000 | 2485000 | 7100000 | 2485000
| - | Temperature Indicator |  | : | SDC15TC0RA0300 [Azbil] |  |  | 2 | pcs | 5138900 | 1798700 | 10277800 | 3597400 |  |  | 3700000 | 1295000 | 7400000 | 2590000
| - | Temperature Sensor |  | : | SPC625B [Azbil] |  |  | 2 | pcs | 5833400 | 2041700 | 11666800 | 4083400 |  |  | 4200000 | 1470000 | 8400000 | 2940000
| - | Cond Temperature Thermostat |  | : | TY6800Z7010 [Azbil] |  |  | 2 | pcs | 7500000 | 2625000 | 15000000 | 5250000 |  |  | 5400000 | 1890000 | 10800000 | 3780000
2 | Inverter For Water Pump
| - | Type |  | : | ACH580-01-293A IP55 |  |  | 1 | unit | 190937700 | 28640700 | 190937700 | 28640700 |  |  | 137475080 | 20621262 | 137475080 | 20621262
|  | Power |  | : | 160 kW
3 | Watercooled Chiller -1 [CH-1]
| - | Cable Power CH-1 NYY 9x (1C x 150 mm²) | [5 empty] | 10 | mtr | 8383400 | 3353400 | 83834000 | 33534000 |  |  | 6036000 | 2414400 | 60360000 | 24144000 | 503000
| - | Cabel Control CH-1 Shielded (10C x 1.5 mm²) | [5 empty] | 10 | mtr | 101400 | 40600 | 1014000 | 406000 |  |  | 73000 | 29200 | 730000 | 292000 | 386329
| - | Cabel Control Motorized Valve Pipe CWP1 Shielded (8C x 1.5 mm²) | [5 empty] | 0 | mtr | 61200 | 24500 | 0 | 0 |  |  | 44000 | 17600 | 0 | 0 | 1.302
| - | Cabel Control Motorized Valve Pipe CDP1 Shielded (8C x 1.5 mm²) | [5 empty] | 0 | mtr | 61200 | 24500 | 0 | 0 |  |  | 44000 | 17600 | 0 | 0
4 | Watercooled Chiller -2 [CH-2]
| - | Cable Power CH-1 NYY 9x (1C x 150 mm²) | [5 empty] | 20 | mtr | 8383400 | 3353400 | 167668000 | 67068000 |  |  | 6036000 | 2414400 | 120720000 | 48288000
| - | Cabel Control CH-2 Shielded (10C x 1.5 mm²) | [5 empty] | 25 | mtr | 101400 | 40600 | 2535000 | 1015000 |  |  | 73000 | 29200 | 1825000 | 730000
| - | Cabel Control Motorized Valve Pipe CWP2 Shielded (8C x 1.5 mm²) | [5 empty] | 0 | mtr | 61200 | 24500 | 0 | 0 |  |  | 44000 | 17600 | 0 | 0
| - | Cabel Control Motorized Valve Pipe CDP2 Shielded (8C x 1.5 mm²) | [5 empty] | 0 | mtr | 61200 | 24500 | 0 | 0 |  |  | 44000 | 17600 | 0 | 0
5 | Watercooled Chiller -3 [CH-3]
| - | Cable Power CH-1 NYY 9x (1C x 150 mm²) | [5 empty] | 15 | mtr | 8383400 | 3353400 | 125751000 | 50301000 |  |  | 6036000 | 2414400 | 90540000 | 36216000
| - | Cabel Control CH-3 Shielded AWG24 (10C x 1.5 mm²) | [5 empty] | 15 | mtr | 101400 | 40600 | 1521000 | 609000 |  |  | 73000 | 29200 | 1095000 | 438000
| - | Cabel Control Motorized Valve Pipe CWP3 Shielded (8C x 1.5 mm²) | [5 empty] | 0 | mtr | 61200 | 24500 | 0 | 0 |  |  | 44000 | 17600 | 0 | 0
| - | Cabel Control Motorized Valve Pipe CDP3 Shielded (8C x 1.5 mm²) | [5 empty] | 0 | mtr | 61200 | 24500 | 0 | 0 |  |  | 44000 | 17600 | 0 | 0
| - | Cabel Control Pressure Sensor PE2 Shielded (2C x 1.5 mm²) | [5 empty] | 50 | mtr | 43100 | 17300 | 2155000 | 865000 |  |  | 31000 | 12400 | 1550000 | 620000
| - | Cabel Control Sensor Temperature T1 D Shielded (2C x 1.5 mm²) | [5 empty] | 60 | mtr | 43100 | 17300 | 2586000 | 1038000 |  |  | 31000 | 12400 | 1860000 | 744000
| - | Cabel Control Sensor Temperature T2 D Shielded (2C x 1.5 mm²) | [5 empty] | 60 | mtr | 43100 | 17300 | 2586000 | 1038000 |  |  | 31000 | 12400 | 1860000 | 744000
| - | Cabel Control Sensor Temperature TC 1~3 D Shielded 3x(8C x 1.5 mm²) | [5 empty] | 60 | mtr | 183400 | 73400 | 11004000 | 4404000 |  |  | 132000 | 52800 | 7920000 | 3168000
12 | Cooling Tower-1 [CT-1]
| - | Cable Power Fan-1 CT-1 NYY 2x(3C x 4 mm²) + NYA (1C x 16 mm²) | [5 empty] | 55 | mtr | 294500 | 117800 | 16197500 | 6479000 |  |  | 212000 | 84800 | 11660000 | 4664000
13 | Cooling Tower-2 [CT-2]
| - | Cable Power Fan-1 CT-1 NYY 2x(3C x 4 mm²)+ NYA (1C x 16 mm²) | [5 empty] | 45 | mtr | 294500 | 117800 | 13252500 | 5301000 |  |  | 212000 | 84800 | 9540000 | 3816000
14 | Cooling Tower-3 [CT-3]
| - | Cable Power Fan-1 CT-1 NYY 2x(3C x 4 mm²)+ NYA (1C x 16 mm²) | [5 empty] | 40 | mtr | 294500 | 117800 | 11780000 | 4712000 |  |  | 212000 | 84800 | 8480000 | 3392000
16 | Water Pump
| - | Cable Power Primary Chiller Water Pump [CWP 1-1] NYY 2x(3C x 6 mm²) + NYA (1C x 25 mm²) | [5 empty] | 50 | mtr | 408400 | 163400 | 20420000 | 8170000 |  |  | 294000 | 117600 | 14700000 | 5880000
| - | Cable Power Primary Chiller Water Pump [CWP 1-2] NYY 2x(3C x 6 mm²)+ NYA (1C x 25 mm²) | [5 empty] | 55 | mtr | 408400 | 163400 | 22462000 | 8987000 |  |  | 294000 | 117600 | 16170000 | 6468000
| - | Cable Power Primary Chiller Water Pump [CWP 1-3] NYY 2x(3C x 6 mm²)+ NYA (1C x 25 mm²) | [5 empty] | 60 | mtr | 408400 | 163400 | 24504000 | 9804000 |  |  | 294000 | 117600 | 17640000 | 7056000
| - | Cable Power Secondary Chiller Water Pump [CWP 2-1] NYY 2x(3C x 150 mm²) +NYA (1C x 70mm²) | [5 empty] | 65 | mtr | 4650000 | 1860000 | 302250000 | 120900000 |  |  | 3348000 | 1339200 | 217620000 | 87048000
| - | Cable Power Condenser Water Pump [CDP 1] NYY 2x(3C x 16 mm²) + (NYA 1C x 25 mm²) | [5 empty] | 45 | mtr | 1013900 | 405600 | 45625500 | 18252000 |  |  | 730000 | 292000 | 32850000 | 13140000
| - | Cable Power Condenser Water Pump [CDP 2] NYY 2x(3C x 16 mm²) + (NYA 1C x 25 mm²) | [5 empty] | 45 | mtr | 1013900 | 405600 | 45625500 | 18252000 |  |  | 730000 | 292000 | 32850000 | 13140000
| - | Cable Power Condenser Water Pump [CDP 2] NYY 2x(3C x 16 mm²)+ (NYA 1C x 25 mm²) | [5 empty] | 45 | mtr | 1013900 | 405600 | 45625500 | 18252000 |  |  | 730000 | 292000 | 32850000 | 13140000
17 | Inverter Water Pump
| - | Cable Power Inverter Water Pump [VFD 1-1] NYY (3C x 150 mm²) + (NYA 1C x 70 mm²) | [5 empty] | 35 | mtr | 1023700 | 409500 | 35829500 | 14332500 |  |  | 737000 | 294800 | 25795000 | 10318000
| - | Cabel Control Sensor Temperature T 1 Shielded (8C x 1.5 mm²) | [5 empty] | 60 | mtr | 61200 | 24500 | 3672000 | 1470000 |  |  | 44000 | 17600 | 2640000 | 1056000
| - | Cable Ladder ( 1000 mm x 100 mm ) include with cover | [5 empty] | 38 | mtr | 735200 | 294100 | 27937600 | 11175800 |  |  | 529333.3333 | 211733.3333 | 20114666.6667 | 8045866.6667
| - | Cable Incoming Chiller 12x(1C x 150 mm²) (Material By User) | [5 empty] | 0 | mtr | 10479200 | 4191700 | 0 | 0 |  |  | 7545000 | 3018000 | 0 | 0
[7 empty] | SUB TOTAL INSTALLATION ELECTRICAL |  |  |  |  | 1287051400 | 463103500 |  |  |  |  | 926644746.6667 | 333399128.6667
C | Lifting & Civil Installation
1 | Lifting
| - | Lifting Unit Chiller Watercooled | [5 empty] | 3 | Unit | 32000000 | 12800000 | 96000000 | 38400000 |  |  | 0 | 0 | 0 | 0
| - | Lifting Unit Cooling Tower | [5 empty] | 3 | Unit | 15335700 | 6134300 | 46007100 | 18402900 |  |  | 11041666.675 | 4416666.67 | 33125000.025 | 13250000.01
| - | Lifting Unit Water Pump | [5 empty] | 7 | Unit | 9279000 | 3711600 | 64953000 | 25981200 |  |  | 6680833.3333 | 2672333.3333 | 46765833.3333 | 18706333.3333
| - | Lifting Unit Panel Operational | [5 empty] | 4 | Unit | 31250000 | 12500000 | 125000000 | 50000000 |  |  | 22500000 | 9000000 | 90000000 | 36000000
[7 empty] | SUB TOTAL PEKERJAAN LIFTING |  |  |  |  | 331960100 | 132784100 |  |  |  |  | 169890833.3583 | 67956333.3433
|  |  | Noted : Tambah Valve 8"x2 | [5 empty] | SUMMARY : | [5 empty] | SUMMARY :
Pompa Head to 50 Meter
[9 empty] | PRILEMINARY |  |  | 0 | 96875000 |  | PRILEMINARY |  |  | 0 | 77500000
[9 empty] | MAIN EQUIPMENT |  |  | 17625142000 | 223750000 |  | MAIN EQUIPMENT |  |  | 4181780001 | 179000000
[9 empty] | PIPE INSTALLATION |  |  | 5533535500 | 1936780200 |  | PIPE INSTALLATION |  |  | 3984095205 | 1394433321.75
[9 empty] | ELECTRICAL INSTALLATION |  |  | 1287051400 | 463103500 |  | ELECTRICAL INSTALLATION |  |  | 926644746.6667 | 333399128.6667
[9 empty] | LIFTING & CIVIL INSTALLATION |  |  | 331960100 | 132784100 |  | LIFTING & CIVIL INSTALLATION |  |  | 169890833.3583 | 67956333.3433
[7 empty] | TOTAL |  |  |  |  | 24777689000 | 2853292800 | 11.52% |  |  |  | 9262410786.025 | 2052288783.76
[13 empty] | 27630981800 | [5 empty] | 11314699569.785
Margine
16316282230.215
59.05%
15515278213.975
62.62%
8460800000
842970000
1090530000
630124000
2373336000
53334000
3733334000
17184428000